**DRAINAGE CB AND INLET NOTES**

***Unless Otherwise Noted***

1. Catch basin connections and inlet connections shall be 8" diameter. Pipe shall be cement mortar lined ductile iron Class 50 (MIN) per Specification 9-05.2. Fittings shall be cement mortar lined ductile iron. Joints shall be rubber gasket, push-on or mechanical.
2. Bedding shall be Class D with select native material.
3. Catch basin connections shall be placed at a minimum slope of 2% and a maximum slope of 100% per Standard Plan No. 261 and Specification 7-08.3(4).
4. Inlet connections shall be placed at a minimum slope of 5% and a maximum slope of 50% per Specification 7-08.3(5).
5. Catch basins and inlets shall be located per Standard Plan No. 260a and 260b.
6. Television inspection of catch basin connections shall be per Specification 7-17.3(4)I.
7. Contractors are not allowed to core into mains or structures without prior approval from SPU. To schedule core taps, contact SPU at 206-615-0511 a minimum of 48 hours in advance. SPU shall be on site prior to the start of contractor performed core tap. Contractors performing core taps shall provide the coupon of removed material to SPU.