## Headloss Calcs
Project Name: Seattle Public Utilties Example | [9 empty] | Job No.: 8521-47382
Subject: Head Loss Calculation
HL = S X L
Inside Pipe Diameter (in.) |  | 36 | (Force Main) | Headworks elevation | 266
|  |  |  | PS Maximum WSEL | 240
|  |  |  | PS Minimum WSEL | 232
|  |  |  | PS Floor Slab Elevation | 224
|  |  |  | Pump Centerline Elevation | 226.2
|  |  |  | Static Head - Low Level (Suction) | 5.8
|  |  |  | Static Head - High Level (Suction) | 13.8
|  |  |  | Static Head - Low Level (Discharge) | 39.8
|  |  |  | Static Head - Low Level (Discharge) | 39.8
|  |  |  | Static Head (ft.) - Low Level (Suction + Discharge) | 45.6
|  |  |  | Static Head (ft.) - High Level (Suction + Discharge) | 53.6
Q | Q | Velocity | C Value | 140 |  | C Value | 100
|  |  | Headloss (Dynamic) | Total Head - Low Level | Total Head - High Level | Headloss (Dynamic) | Total Head - Low Level | BHP | Total Head - High Level | BHP
MGD | GPM | ft/s | Feet | Feet | Feet | Feet | Feet |  | Feet
1 | 694.4444 | 0.21889 | 0.052559 | 45.6526 | 53.6526 | 0.095696 | 45.6957 | #DIV/0! | 53.6957 | #DIV/0!
2 | 1388.8889 | 0.43777 | 0.1905 | 45.7905 | 53.7905 | 0.34601 | 45.946 | #DIV/0! | 53.946 | #DIV/0!
3 | 2083.3333 | 0.65666 | 0.40472 | 46.0047 | 54.0047 | 0.73397 | 46.334 | #DIV/0! | 54.334 | #DIV/0!
4 | 2777.7778 | 0.87555 | 0.69088 | 46.2909 | 54.2909 | 1.2515 | 46.8515 | #DIV/0! | 54.8515 | #DIV/0!
5 | 3472.2222 | 1.0944 | 1.0461 | 46.6461 | 54.6461 | 1.8932 | 47.4932 | #DIV/0! | 55.4932 | #DIV/0!
6 | 4166.6667 | 1.3133 | 1.4683 | 47.0683 | 55.0683 | 2.6552 | 48.2552 | #DIV/0! | 56.2552 | #DIV/0!
7 | 4861.1111 | 1.5322 | 1.9557 | 47.5557 | 55.5557 | 3.5344 | 49.1344 | #DIV/0! | 57.1344 | #DIV/0!
8 | 5555.5556 | 1.7511 | 2.5071 | 48.1071 | 56.1071 | 4.5281 | 50.1281 | #DIV/0! | 58.1281 | #DIV/0!
9 | 6250 | 1.97 | 3.1211 | 48.7211 | 56.7211 | 5.6342 | 51.2342 | #DIV/0! | 59.2342 | #DIV/0!
10 | 6944.4444 | 2.1889 | 3.7969 | 49.3969 | 57.3969 | 6.8508 | 52.4508 | #DIV/0! | 60.4508 | #DIV/0!
11 | 7638.8889 | 2.4078 | 4.5335 | 50.1335 | 58.1335 | 8.1763 | 53.7763 | #DIV/0! | 61.7763 | #DIV/0!
12 | 8333.3333 | 2.6266 | 5.3302 | 50.9302 | 58.9302 | 9.6091 | 55.2091 | #DIV/0! | 63.2091 | #DIV/0!
13 | 9027.7778 | 2.8455 | 6.1861 | 51.7861 | 59.7861 | 11.148 | 56.748 | #DIV/0! | 64.748 | #DIV/0!
14 | 9722.2222 | 3.0644 | 7.1008 | 52.7008 | 60.7008 | 12.7918 | 58.3918 | #DIV/0! | 66.3918 | #DIV/0!
15 | 10416.6667 | 3.2833 | 8.0735 | 53.6735 | 61.6735 | 14.5393 | 60.1393 | #DIV/0! | 68.1393 | #DIV/0!
16 | 11111.1111 | 3.5022 | 9.1038 | 54.7038 | 62.7038 | 16.3895 | 61.9895 | #DIV/0! | 69.9895 | #DIV/0!
17 | 11805.5556 | 3.7211 | 10.1911 | 55.7911 | 63.7911 | 18.3416 | 63.9416 | #DIV/0! | 71.9416 | #DIV/0!
18 | 12500 | 3.94 | 11.335 | 56.935 | 64.935 | 20.3945 | 65.9945 | #DIV/0! | 73.9945 | #DIV/0!
19 | 13194.4444 | 4.1589 | 12.535 | 58.135 | 66.135 | 22.5476 | 68.1476 | #DIV/0! | 76.1476 | #DIV/0!
20 | 13888.8889 | 4.3777 | 13.7908 | 59.3908 | 67.3908 | 24.8 | 70.4 | #DIV/0! | 78.4 | #DIV/0!
21 | 14583.3333 | 4.5966 | 15.1018 | 60.7018 | 68.7018 | 27.151 | 72.751 | #DIV/0! | 80.751 | #DIV/0!
22 | 15277.7778 | 4.8155 | 16.4678 | 62.0678 | 70.0678 | 29.5999 | 75.1999 | #DIV/0! | 83.1999 | #DIV/0!
23 | 15972.2222 | 5.0344 | 17.8885 | 63.4885 | 71.4885 | 32.1461 | 77.7461 | #DIV/0! | 85.7461 | #DIV/0!
24 | 16666.6667 | 5.2533 | 19.3634 | 64.9634 | 72.9634 | 34.789 | 80.389 | #DIV/0! | 88.389 | #DIV/0!
25 | 17361.1111 | 5.4722 | 20.8923 | 66.4923 | 74.4923 | 37.528 | 83.128 | #DIV/0! | 91.128 | #DIV/0!
26 | 18055.5556 | 5.6911 | 22.4749 | 68.0749 | 76.0749 | 40.3625 | 85.9625 | #DIV/0! | 93.9625 | #DIV/0!
27 | 18750 | 5.91 | 24.1109 | 69.7109 | 77.7109 | 43.292 | 88.892 | #DIV/0! | 96.892 | #DIV/0!
28 | 19444.4444 | 6.1288 | 25.8 | 71.4 | 79.4 | 46.316 | 91.916 | #DIV/0! | 99.916 | #DIV/0!
29 | 20138.8889 | 6.3477 | 27.542 | 73.142 | 81.142 | 49.4341 | 95.0341 | #DIV/0! | 103.0341 | #DIV/0!
30 | 20833.3333 | 6.5666 | 29.3366 | 74.9366 | 82.9366 | 52.6457 | 98.2457 | #DIV/0! | 106.2457 | #DIV/0!
31 | 21527.7778 | 6.7855 | 31.1835 | 76.7835 | 84.7835 | 55.9503 | 101.5503 | #DIV/0! | 109.5503 | #DIV/0!
32 | 22222.2222 | 7.0044 | 33.0826 | 78.6826 | 86.6826 | 59.3477 | 104.9477 | #DIV/0! | 112.9477 | #DIV/0!
33 | 22916.6667 | 7.2233 | 35.0336 | 80.6336 | 88.6336 | 62.8373 | 108.4373 | #DIV/0! | 116.4373 | #DIV/0!
34 | 23611.1111 | 7.4422 | 37.0363 | 82.6363 | 90.6363 | 66.4187 | 112.0187 | #DIV/0! | 120.0187 | #DIV/0!
35 | 24305.5556 | 7.6611 | 39.0905 | 84.6905 | 92.6905 | 70.0916 | 115.6916 | #DIV/0! | 123.6916 | #DIV/0!
36 | 25000 | 7.8799 | 41.196 | 86.796 | 94.796 | 73.8556 | 119.4556 | #DIV/0! | 127.4556 | #DIV/0!
Option B - Powerline Route
Length of Main (ft.) |  | 13750 |  | Plant Elevation | 326 |  |  | HL = S X L
Inside Pipe Diameter (in.) |  | 24 |  | Pump Call | 225 |  |  | S = [Q/.285CD^2.63]^1/0.54
Pump Efficiency |  | 70% |  | Pump Alarm | 246
|  |  |  | Static Head Pump Start (ft.) | 101
|  |  |  | High Level Static Head (ft.) | 80
Q | Q | Velocity | C Value | 130 |  | C Value | 110
|  |  | Headloss (Dynamic) | Total Head - Start Up | Total Head - High Level | Headloss (Dynamic) | Total Head - Start Up | BHP | Total Head - High Level | BHP
MGD | GPM | ft/s | Feet | Feet | Feet | Feet | Feet |  | Feet
1 | 694.4444 | 0.21889 | 0.59332 | 101.5933 | 101.5933 | 0.80843 | 101.8084 | 25.4987 | 80.8084 | 20.2391
1.5 | 1041.6667 | 0.32833 | 1.2571 | 102.2571 | 81.2571 | 1.7129 | 102.7129 | 38.5879 | 81.7129 | 30.6985
2 | 1388.8889 | 0.43777 | 2.1417 | 103.1417 | 82.1417 | 2.9181 | 103.9181 | 52.0542 | 82.9181 | 41.535
2.5 | 1736.1111 | 0.54722 | 3.2376 | 104.2376 | 83.2376 | 4.4113 | 105.4113 | 66.0027 | 84.4113 | 52.8537
3 | 2083.3333 | 0.65666 | 4.5378 | 105.5378 | 84.5378 | 6.183 | 107.183 | 80.5345 | 86.183 | 64.7557
3.5 | 2430.5556 | 0.76611 | 6.037 | 107.037 | 86.037 | 8.2258 | 109.2258 | 95.7476 | 88.2258 | 77.3389
4 | 2777.7778 | 0.87555 | 7.7307 | 108.7307 | 87.7307 | 10.5334 | 111.5334 | 111.7377 | 90.5334 | 90.6992
4.5 | 3125 | 0.98499 | 9.6149 | 110.6149 | 89.6149 | 13.1008 | 114.1008 | 128.5984 | 93.1008 | 104.9302
5 | 3472.2222 | 1.0944 | 11.6864 | 112.6864 | 91.6864 | 15.9233 | 116.9233 | 146.4218 | 95.9233 | 120.1237
5.5 | 3819.4444 | 1.2039 | 13.9423 | 114.9423 | 93.9423 | 18.9971 | 119.9971 | 165.2981 | 98.9971 | 136.3702
6 | 4166.6667 | 1.3133 | 16.3799 | 117.3799 | 96.3799 | 22.3185 | 123.3185 | 185.3165 | 102.3185 | 153.7588
6.5 | 4513.8889 | 1.4228 | 18.9971 | 119.9971 | 98.9971 | 25.8845 | 126.8845 | 206.5649 | 105.8845 | 172.3774
7 | 4861.1111 | 1.5322 | 21.7915 | 122.7915 | 101.7915 | 29.6921 | 130.6921 | 229.13 | 109.6921 | 192.3127
7.5 | 5208.3333 | 1.6417 | 24.7614 | 125.7614 | 104.7614 | 33.7387 | 134.7387 | 253.0977 | 113.7387 | 213.6506
8 | 5555.5556 | 1.7511 | 27.9049 | 128.9049 | 107.9049 | 38.0218 | 139.0218 | 278.5529 | 118.0218 | 236.4759
8.5 | 5902.7778 | 1.8605 | 31.2203 | 132.2203 | 111.2203 | 42.5393 | 143.5393 | 305.5796 | 122.5393 | 260.8729
9 | 6250 | 1.97 | 34.7062 | 135.7062 | 114.7062 | 47.289 | 148.289 | 334.2612 | 127.289 | 286.9247
9.5 | 6597.2222 | 2.0794 | 38.361 | 139.361 | 118.361 | 52.2689 | 153.2689 | 364.6803 | 132.2689 | 314.714
10 | 6944.4444 | 2.1889 | 42.1835 | 143.1835 | 122.1835 | 57.4773 | 158.4773 | 396.9187 | 137.4773 | 344.3226
10.5 | 7291.6667 | 2.2983 | 46.1724 | 147.1724 | 126.1724 | 62.9123 | 163.9123 | 431.0577 | 142.9123 | 375.8318
11 | 7638.8889 | 2.4078 | 50.3264 | 151.3264 | 130.3264 | 68.5724 | 169.5724 | 467.178 | 148.5724 | 409.3223
11.5 | 7986.1111 | 2.5172 | 54.6445 | 155.6445 | 134.6445 | 74.456 | 175.456 | 505.3597 | 154.456 | 444.8741
12 | 8333.3333 | 2.6266 | 59.1255 | 160.1255 | 139.1255 | 80.5616 | 181.5616 | 545.6822 | 160.5616 | 482.5669
12.5 | 8680.5556 | 2.7361 | 63.7685 | 164.7685 | 143.7685 | 86.8878 | 187.8878 | 588.2248 | 166.8878 | 522.4796
13 | 9027.7778 | 2.8455 | 68.5724 | 169.5724 | 148.5724 | 93.4334 | 194.4334 | 633.0659 | 173.4334 | 564.6909
13.5 | 9375 | 2.955 | 73.5363 | 174.5363 | 153.5363 | 100.197 | 201.197 | 680.2835 | 180.197 | 609.2787
14 | 9722.2222 | 3.0644 | 78.6594 | 179.6594 | 158.6594 | 107.1775 | 208.1775 | 729.9555 | 187.1775 | 656.3209
14.5 | 10069.4444 | 3.1739 | 83.9407 | 184.9407 | 163.9407 | 114.3736 | 215.3736 | 782.159 | 194.3736 | 705.8945
15 | 10416.6667 | 3.2833 | 89.3795 | 190.3795 | 169.3795 | 121.7842 | 222.7842 | 836.9707 | 201.7842 | 758.0765

## Station Piping
This example calculation spreadsheet has not been reviewed or approved for wide use. It is provided as informational only. The engineer may use this information, but it should be thoroughly checked.
Project Name: Seattle Public Utilties Example
Subject: Head Loss Calculation
Note: A values in red are system parameters to be changed.
Force Main Sizing |  |  |  |  | Velocity in Force Main at Design Points
Inside Pipe Diameter (in.) |  | 36
[5 empty] | Inside Pipe Diameter (in.) |  | 36
Q | Q | Velocity |  |  | Q | Q | Velocity | Comment
MGD | GPM | ft/s |  |  | MGD | GPM | ft/s
33 | 22916.6667 | 7.2233 |  |  | 4 | 2777.7778 | 0.87555 | Low
[5 empty] | 7 | 4861.1111 | 1.5322 | Low
[5 empty] | 10 | 6944.4444 | 2.1889 | Acceptable
[5 empty] | 20 | 13888.8889 | 4.3777 | Acceptable
Discharge Piping
Larger Submersible
Inside Pipe Diameter (in.) |  | 16 | Trial #1
Inside Pipe Diameter (in.) |  | 18 | Trial #2
| Q | Q | Velocity | Comment
| MGD | CFS | ft/s
Trial #1 | 8.25 | 12.7655 | 9.1426 | High
Trial #2 | 8.25 | 12.7655 | 7.2238 | Acceptable
Note: Velocity should selected based on 6 to 10 fps.
Station Losses Calculations
Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
18 | Pump | 8.25 | 12.7655 | 140 | 1.7671 | 4.7124 | 0.375 | 7.2238 | 0 | 0 | 0 | 0
14 | 14" X 18" Increaser | 8.25 | 12.7655 | 140 | 1.069 | 3.6652 | 0.29167 | 11.9414 | 0.35 | 0.77498 | 0.77498 | 0.77498
18 | 90 Deg Bend | 8.25 | 12.7655 | 140 | 1.7671 | 4.7124 | 0.375 | 7.2238 | 0.2 | 0.16206 | 0.16206 | 0.93704
18 | 90 Deg Bend | 8.25 | 12.7655 | 140 | 1.7671 | 4.7124 | 0.375 | 7.2238 | 0.2 | 0.16206 | 0.16206 | 1.0991
18 | Check Valve | 8.25 | 12.7655 | 140 | 1.7671 | 4.7124 | 0.375 | 7.2238 | 2.5 | 2.0257 | 2.0257 | 3.1248
18 | Plug Valve | 8.25 | 12.7655 | 140 | 1.7671 | 4.7124 | 0.375 | 7.2238 | 0.91 | 0.73737 | 0.73737 | 3.8622
18 | Branch Tee | 8.25 | 12.7655 | 140 | 1.7671 | 4.7124 | 0.375 | 7.2238 | 1.8 | 1.4585 | 1.4585 | 5.3207
18 | Flow thru Tee | 8.25 | 12.7655 | 140 | 1.7671 | 4.7124 | 0.375 | 7.2238 | 0.6 | 0.48618 | 0.48618 | 5.8069
[11 empty] | Total | 5.8069
Note: Increaser is necessary since velocity is excessive for 14" diameter.
Small Pump
Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
10 | Pump | 3.25 | 5.0288 | 140 | 0.54542 | 2.618 | 0.20833 | 9.2202 | 0 | 0 | 0 | 0
10 | 14" X 18" Increaser | 3.25 | 5.0288 | 140 | 0.54542 | 2.618 | 0.20833 | 9.2202 | 0.35 | 0.46202 | 0.46202 | 0.46202
10 | 90 Deg Bend | 3.25 | 5.0288 | 140 | 0.54542 | 2.618 | 0.20833 | 9.2202 | 0.2 | 0.26401 | 0.26401 | 0.72603
10 | 90 Deg Bend | 3.25 | 5.0288 | 140 | 0.54542 | 2.618 | 0.20833 | 9.2202 | 0.2 | 0.26401 | 0.26401 | 0.99004
10 | Check Valve | 3.25 | 5.0288 | 140 | 0.54542 | 2.618 | 0.20833 | 9.2202 | 2.5 | 3.3001 | 3.3001 | 4.2902
10 | Plug Valve | 3.25 | 5.0288 | 140 | 0.54542 | 2.618 | 0.20833 | 9.2202 | 0.85 | 1.1221 | 1.1221 | 5.4122
10 | Branch Tee | 3.25 | 5.0288 | 140 | 0.54542 | 2.618 | 0.20833 | 9.2202 | 1.8 | 2.3761 | 2.3761 | 7.7883
10 | Flow thru Tee | 3.25 | 5.0288 | 140 | 0.54542 | 2.618 | 0.20833 | 9.2202 | 0.6 | 0.79204 | 0.79204 | 8.5804
Station Losses (Discharge Piping)
Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Pipe Length | Head Loss
18 | Pump | 8.25 | 12.7655 | 140 | 1.7671 | 4.7124 | 0.375 | 7.2238 | 30 | 0.23449
36 | Pump | 8.25 | 12.7655 | 140 | 7.0686 | 9.4248 | 0.75 | 1.8059 | 50 | 0.013406
[9 empty] | Total | 0.2479
Small Pump
Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Pipe Length | Head Loss
10 | Pump | 3.25 | 5.0288 | 140 | 0.54542 | 2.618 | 0.20833 | 9.2202 | 30 | 0.73063
36 | Pump | 3.25 | 5.0288 | 140 | 7.0686 | 9.4248 | 0.75 | 0.71143 | 50 | 0.0023925
[9 empty] | Total | 0.73302
Total Station losses for large pump |  |  | 6.0548
Total Station losses for small pump |  |  | 0.73302
Force Main Layout Losses
Force Main Piping Losses
Diameter (in) | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Pipe Length | Head Loss
36 | 33 | 51.0621 | 140 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 10560 | 36.7972
[8 empty] | Total | 36.7972
Misc Fittings Losses
Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Minor Loss K Coefficient | Minor Loss | Total Head Loss
36 | 90 Deg Bend | 33 | 51.0621 | 140 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 0.2 | 0.16206 | 0.16206
36 | 90 Deg Bend | 33 | 51.0621 | 140 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 0.2 | 0.16206 | 0.16206
36 | 45 Deg Bend | 33 | 51.0621 | 140 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 0.4 | 0.32412 | 0.32412
36 | 45 Deg Bend | 33 | 51.0621 | 140 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 0.4 | 0.32412 | 0.32412
36 | 45 Deg Bend | 33 | 51.0621 | 140 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 0.4 | 0.32412 | 0.32412
30 | 36" X 30" Reducer | 33 | 51.0621 | 140 | 4.9087 | 7.854 | 0.625 | 10.4023 | 0.25 | 0.42006 | 0.42006
30 | 30" X 36" Increaser | 33 | 51.0621 | 140 | 4.9087 | 7.854 | 0.625 | 10.4023 | 0.26 | 0.43686 | 0.43686
36 | HW Discharge | 33 | 51.0621 | 140 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 1 | 0.8103 | 0.8103
[10 empty] | Total | 2.9637
Total Force Main Losses |  | 39.7609

## Pump Characterstics
One Pumps Operating |  |  |  |  | Two Pumps Operating
Flow (MGD) | Head (ft) | Station Losses |  | Modified curve | Flow (MGD) | Head (ft) | Station Losses |  | Modified curve
|  | Flow | Headloss |  |  |  | Flow | Headloss
0 | 105 | 0 | 0 | 105 | 0 | 105 | 0 | 0 | 105
4.95 | 87.9 | 0.36 | 2.1797 | 85.7203 | 9.9 | 87.9 | 0.36 | 2.1797 | 85.7203
6.6 | 83.3 | 0.64 | 3.8751 | 79.4249 | 13.2 | 83.3 | 0.64 | 3.8751 | 79.4249
8.25 | 78.7 | 1 | 6.0548 | 72.6452 | 16.5 | 78.7 | 1 | 6.0548 | 72.6452
9.9 | 74.4 | 1.44 | 8.7189 | 65.6811 | 19.8 | 74.4 | 1.44 | 8.7189 | 65.6811
11.5 | 66.1 | 1.9431 | 11.7649 | 54.3351 | 23 | 66.1 | 1.9431 | 11.7649 | 54.3351
13.3 | 55.1 | 2.5989 | 15.7361 | 39.3639 | 26.6 | 55.1 | 2.5989 | 15.7361 | 39.3639
14.5 | 46.8 | 3.0891 | 18.7038 | 28.0962 | 29 | 46.8 | 3.0891 | 18.7038 | 28.0962
Three Pumps Operating |  |  |  |  | Four Pumps Operating
Flow (MGD) | Head (ft) | Station Losses |  | Modified curve | Flow | Head (ft) | Station Losses |  | Modified curve
|  | Flow | Headloss |  |  |  | Flow | Headloss
0 | 105 | 0 | 0 | 105 | 0 | 105 | 0 | 0 | 105
14.85 | 87.9 | 0.36 | 2.1797 | 85.7203 | 19.8 | 87.9 | 0.36 | 2.1797 | 85.7203
19.8 | 83.3 | 0.64 | 3.8751 | 79.4249 | 26.4 | 83.3 | 0.64 | 3.8751 | 79.4249
24.75 | 78.7 | 1 | 6.0548 | 72.6452 | 33 | 78.7 | 1 | 6.0548 | 72.6452
29.7 | 74.4 | 1.44 | 8.7189 | 65.6811 | 39.6 | 74.4 | 1.44 | 8.7189 | 65.6811
34.5 | 66.1 | 1.9431 | 11.7649 | 54.3351 | 46 | 66.1 | 1.9431 | 11.7649 | 54.3351
39.9 | 55.1 | 2.5989 | 15.7361 | 39.3639 | 53.2 | 55.1 | 2.5989 | 15.7361 | 39.3639
43.5 | 46.8 | 3.0891 | 18.7038 | 28.0962 | 58 | 46.8 | 3.0891 | 18.7038 | 28.0962
Note: Head numbers are provided by manufacturer's pump data.

## HL 1.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 1 | 1.5473 | 140 | 7.0686 | 9.4248 | 0.75 | 0.2189 | 0 | 0.25 | 0.00018602 | 0.00018602 | 0.00018602
| 36 | 30" X 36" Increaser | 1 | 1.5473 | 140 | 7.0686 | 9.4248 | 0.75 | 0.2189 | 0 | 0.25 | 0.00018602 | 0.00018602 | 0.00037204
1320 | 36 | Pipe | 1 | 1.5473 | 140 | 7.0686 | 9.4248 | 0.75 | 0.2189 | 0.0071363 |  | 0 | 0.0071363 | 0.0075084
| 36 | 90 Deg Bend | 1 | 1.5473 | 140 | 7.0686 | 9.4248 | 0.75 | 0.2189 | 0 | 0.2 | 0.00014881 | 0.00014881 | 0.0076572
1320 | 36 | Pipe | 1 | 1.5473 | 140 | 7.0686 | 9.4248 | 0.75 | 0.2189 | 0.0071363 |  | 0 | 0.0071363 | 0.014793
| 36 | 45 Deg Bend | 1 | 1.5473 | 140 | 7.0686 | 9.4248 | 0.75 | 0.2189 | 0 | 0.4 | 0.00029763 | 0.00029763 | 0.015091
1320 | 36 | Pipe | 1 | 1.5473 | 140 | 7.0686 | 9.4248 | 0.75 | 0.2189 | 0.0071363 |  | 0 | 0.0071363 | 0.022227
| 36 | 45 Deg Bend | 1 | 1.5473 | 140 | 7.0686 | 9.4248 | 0.75 | 0.2189 | 0 | 0.4 | 0.00029763 | 0.00029763 | 0.022525
1320 | 36 | Pipe | 1 | 1.5473 | 140 | 7.0686 | 9.4248 | 0.75 | 0.2189 | 0.0071363 |  | 0 | 0.0071363 | 0.029661
| 36 | 45 Deg Bend | 1 | 1.5473 | 140 | 7.0686 | 9.4248 | 0.75 | 0.2189 | 0 | 0.4 | 0.00029763 | 0.00029763 | 0.029959
1320 | 36 | Pipe | 1 | 1.5473 | 140 | 7.0686 | 9.4248 | 0.75 | 0.2189 | 0.0071363 |  | 0 | 0.0071363 | 0.037095
| 36 | 45 Deg Bend | 1 | 1.5473 | 140 | 7.0686 | 9.4248 | 0.75 | 0.2189 | 0 | 0.4 | 0.00029763 | 0.00029763 | 0.037393
1320 | 36 | Pipe | 1 | 1.5473 | 140 | 7.0686 | 9.4248 | 0.75 | 0.2189 | 0.0071363 |  | 0 | 0.0071363 | 0.044529
| 36 | 90 Deg Bend | 1 | 1.5473 | 140 | 7.0686 | 9.4248 | 0.75 | 0.2189 | 0 | 0.2 | 0.00014881 | 0.00014881 | 0.044678
1320 | 36 | Pipe | 1 | 1.5473 | 140 | 7.0686 | 9.4248 | 0.75 | 0.2189 | 0.0071363 |  | 0 | 0.0071363 | 0.051814
| 36 | Exit to Headworks | 1 | 1.5473 | 140 | 7.0686 | 9.4248 | 0.75 | 0.2189 | 0 | 1 | 0.00074407 | 0.00074407 | 0.052559
[13 empty] | Total | 0.052559
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 1 | 1.5473 | 100 | 7.0686 | 9.4248 | 0.75 | 0.2189 | 0 | 0.25 | 0.00018602 | 0.00018602 | 0.00018602
| 36 | 30" X 36" Increaser | 1 | 1.5473 | 100 | 7.0686 | 9.4248 | 0.75 | 0.2189 | 0 | 0.25 | 0.00018602 | 0.00018602 | 0.00037204
1320 | 36 | Pipe | 1 | 1.5473 | 100 | 7.0686 | 9.4248 | 0.75 | 0.2189 | 0.013299 |  | 0 | 0.013299 | 0.013671
| 36 | 90 Deg Bend | 1 | 1.5473 | 100 | 7.0686 | 9.4248 | 0.75 | 0.2189 | 0 | 0.2 | 0.00014881 | 0.00014881 | 0.01382
1320 | 36 | Pipe | 1 | 1.5473 | 100 | 7.0686 | 9.4248 | 0.75 | 0.2189 | 0.013299 |  | 0 | 0.013299 | 0.027118
| 36 | 45 Deg Bend | 1 | 1.5473 | 100 | 7.0686 | 9.4248 | 0.75 | 0.2189 | 0 | 0.4 | 0.00029763 | 0.00029763 | 0.027416
1320 | 36 | Pipe | 1 | 1.5473 | 100 | 7.0686 | 9.4248 | 0.75 | 0.2189 | 0.013299 |  | 0 | 0.013299 | 0.040715
| 36 | 45 Deg Bend | 1 | 1.5473 | 100 | 7.0686 | 9.4248 | 0.75 | 0.2189 | 0 | 0.4 | 0.00029763 | 0.00029763 | 0.041012
1320 | 36 | Pipe | 1 | 1.5473 | 100 | 7.0686 | 9.4248 | 0.75 | 0.2189 | 0.013299 |  | 0 | 0.013299 | 0.054311
| 36 | 45 Deg Bend | 1 | 1.5473 | 100 | 7.0686 | 9.4248 | 0.75 | 0.2189 | 0 | 0.4 | 0.00029763 | 0.00029763 | 0.054609
1320 | 36 | Pipe | 1 | 1.5473 | 100 | 7.0686 | 9.4248 | 0.75 | 0.2189 | 0.013299 |  | 0 | 0.013299 | 0.067908
| 36 | 45 Deg Bend | 1 | 1.5473 | 100 | 7.0686 | 9.4248 | 0.75 | 0.2189 | 0 | 0.4 | 0.00029763 | 0.00029763 | 0.068205
1320 | 36 | Pipe | 1 | 1.5473 | 100 | 7.0686 | 9.4248 | 0.75 | 0.2189 | 0.013299 |  | 0 | 0.013299 | 0.081504
| 36 | 90 Deg Bend | 1 | 1.5473 | 100 | 7.0686 | 9.4248 | 0.75 | 0.2189 | 0 | 0.2 | 0.00014881 | 0.00014881 | 0.081653
1320 | 36 | Pipe | 1 | 1.5473 | 100 | 7.0686 | 9.4248 | 0.75 | 0.2189 | 0.013299 |  | 0 | 0.013299 | 0.094952
| 36 | Exit to Headworks | 1 | 1.5473 | 100 | 7.0686 | 9.4248 | 0.75 | 0.2189 | 0 | 1 | 0.00074407 | 0.00074407 | 0.095696
[13 empty] | Total | 0.095696

## HL 2.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 2 | 3.0947 | 140 | 7.0686 | 9.4248 | 0.75 | 0.43781 | 0 | 0.25 | 0.00074407 | 0.00074407 | 0.00074407
| 36 | 30" X 36" Increaser | 2 | 3.0947 | 140 | 7.0686 | 9.4248 | 0.75 | 0.43781 | 0 | 0.25 | 0.00074407 | 0.00074407 | 0.0014881
1320 | 36 | Pipe | 2 | 3.0947 | 140 | 7.0686 | 9.4248 | 0.75 | 0.43781 | 0.025726 |  | 0 | 0.025726 | 0.027215
| 36 | 90 Deg Bend | 2 | 3.0947 | 140 | 7.0686 | 9.4248 | 0.75 | 0.43781 | 0 | 0.2 | 0.00059526 | 0.00059526 | 0.02781
1320 | 36 | Pipe | 2 | 3.0947 | 140 | 7.0686 | 9.4248 | 0.75 | 0.43781 | 0.025726 |  | 0 | 0.025726 | 0.053536
| 36 | 45 Deg Bend | 2 | 3.0947 | 140 | 7.0686 | 9.4248 | 0.75 | 0.43781 | 0 | 0.4 | 0.0011905 | 0.0011905 | 0.054727
1320 | 36 | Pipe | 2 | 3.0947 | 140 | 7.0686 | 9.4248 | 0.75 | 0.43781 | 0.025726 |  | 0 | 0.025726 | 0.080453
| 36 | 45 Deg Bend | 2 | 3.0947 | 140 | 7.0686 | 9.4248 | 0.75 | 0.43781 | 0 | 0.4 | 0.0011905 | 0.0011905 | 0.081644
1320 | 36 | Pipe | 2 | 3.0947 | 140 | 7.0686 | 9.4248 | 0.75 | 0.43781 | 0.025726 |  | 0 | 0.025726 | 0.10737
| 36 | 45 Deg Bend | 2 | 3.0947 | 140 | 7.0686 | 9.4248 | 0.75 | 0.43781 | 0 | 0.4 | 0.0011905 | 0.0011905 | 0.10856
1320 | 36 | Pipe | 2 | 3.0947 | 140 | 7.0686 | 9.4248 | 0.75 | 0.43781 | 0.025726 |  | 0 | 0.025726 | 0.13429
| 36 | 45 Deg Bend | 2 | 3.0947 | 140 | 7.0686 | 9.4248 | 0.75 | 0.43781 | 0 | 0.4 | 0.0011905 | 0.0011905 | 0.13548
1320 | 36 | Pipe | 2 | 3.0947 | 140 | 7.0686 | 9.4248 | 0.75 | 0.43781 | 0.025726 |  | 0 | 0.025726 | 0.1612
| 36 | 90 Deg Bend | 2 | 3.0947 | 140 | 7.0686 | 9.4248 | 0.75 | 0.43781 | 0 | 0.2 | 0.00059526 | 0.00059526 | 0.1618
1320 | 36 | Pipe | 2 | 3.0947 | 140 | 7.0686 | 9.4248 | 0.75 | 0.43781 | 0.025726 |  | 0 | 0.025726 | 0.18753
| 36 | Exit to Headworks | 2 | 3.0947 | 140 | 7.0686 | 9.4248 | 0.75 | 0.43781 | 0 | 1 | 0.0029763 | 0.0029763 | 0.1905
[13 empty] | Total | 0.1905
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 2 | 3.0947 | 100 | 7.0686 | 9.4248 | 0.75 | 0.43781 | 0 | 0.25 | 0.00074407 | 0.00074407 | 0.00074407
| 36 | 30" X 36" Increaser | 2 | 3.0947 | 100 | 7.0686 | 9.4248 | 0.75 | 0.43781 | 0 | 0.25 | 0.00074407 | 0.00074407 | 0.0014881
1320 | 36 | Pipe | 2 | 3.0947 | 100 | 7.0686 | 9.4248 | 0.75 | 0.43781 | 0.047942 |  | 0 | 0.047942 | 0.04943
| 36 | 90 Deg Bend | 2 | 3.0947 | 100 | 7.0686 | 9.4248 | 0.75 | 0.43781 | 0 | 0.2 | 0.00059526 | 0.00059526 | 0.050025
1320 | 36 | Pipe | 2 | 3.0947 | 100 | 7.0686 | 9.4248 | 0.75 | 0.43781 | 0.047942 |  | 0 | 0.047942 | 0.097968
| 36 | 45 Deg Bend | 2 | 3.0947 | 100 | 7.0686 | 9.4248 | 0.75 | 0.43781 | 0 | 0.4 | 0.0011905 | 0.0011905 | 0.099158
1320 | 36 | Pipe | 2 | 3.0947 | 100 | 7.0686 | 9.4248 | 0.75 | 0.43781 | 0.047942 |  | 0 | 0.047942 | 0.1471
| 36 | 45 Deg Bend | 2 | 3.0947 | 100 | 7.0686 | 9.4248 | 0.75 | 0.43781 | 0 | 0.4 | 0.0011905 | 0.0011905 | 0.14829
1320 | 36 | Pipe | 2 | 3.0947 | 100 | 7.0686 | 9.4248 | 0.75 | 0.43781 | 0.047942 |  | 0 | 0.047942 | 0.19623
| 36 | 45 Deg Bend | 2 | 3.0947 | 100 | 7.0686 | 9.4248 | 0.75 | 0.43781 | 0 | 0.4 | 0.0011905 | 0.0011905 | 0.19742
1320 | 36 | Pipe | 2 | 3.0947 | 100 | 7.0686 | 9.4248 | 0.75 | 0.43781 | 0.047942 |  | 0 | 0.047942 | 0.24537
| 36 | 45 Deg Bend | 2 | 3.0947 | 100 | 7.0686 | 9.4248 | 0.75 | 0.43781 | 0 | 0.4 | 0.0011905 | 0.0011905 | 0.24656
1320 | 36 | Pipe | 2 | 3.0947 | 100 | 7.0686 | 9.4248 | 0.75 | 0.43781 | 0.047942 |  | 0 | 0.047942 | 0.2945
| 36 | 90 Deg Bend | 2 | 3.0947 | 100 | 7.0686 | 9.4248 | 0.75 | 0.43781 | 0 | 0.2 | 0.00059526 | 0.00059526 | 0.29509
1320 | 36 | Pipe | 2 | 3.0947 | 100 | 7.0686 | 9.4248 | 0.75 | 0.43781 | 0.047942 |  | 0 | 0.047942 | 0.34304
| 36 | Exit to Headworks | 2 | 3.0947 | 100 | 7.0686 | 9.4248 | 0.75 | 0.43781 | 0 | 1 | 0.0029763 | 0.0029763 | 0.34601
[13 empty] | Total | 0.34601

## HL 3.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 3 | 4.642 | 140 | 7.0686 | 9.4248 | 0.75 | 0.65671 | 0 | 0.25 | 0.0016742 | 0.0016742 | 0.0016742
| 36 | 30" X 36" Increaser | 3 | 4.642 | 140 | 7.0686 | 9.4248 | 0.75 | 0.65671 | 0 | 0.25 | 0.0016742 | 0.0016742 | 0.0033483
1320 | 36 | Pipe | 3 | 4.642 | 140 | 7.0686 | 9.4248 | 0.75 | 0.65671 | 0.054469 |  | 0 | 0.054469 | 0.057817
| 36 | 90 Deg Bend | 3 | 4.642 | 140 | 7.0686 | 9.4248 | 0.75 | 0.65671 | 0 | 0.2 | 0.0013393 | 0.0013393 | 0.059157
1320 | 36 | Pipe | 3 | 4.642 | 140 | 7.0686 | 9.4248 | 0.75 | 0.65671 | 0.054469 |  | 0 | 0.054469 | 0.11363
| 36 | 45 Deg Bend | 3 | 4.642 | 140 | 7.0686 | 9.4248 | 0.75 | 0.65671 | 0 | 0.4 | 0.0026787 | 0.0026787 | 0.1163
1320 | 36 | Pipe | 3 | 4.642 | 140 | 7.0686 | 9.4248 | 0.75 | 0.65671 | 0.054469 |  | 0 | 0.054469 | 0.17077
| 36 | 45 Deg Bend | 3 | 4.642 | 140 | 7.0686 | 9.4248 | 0.75 | 0.65671 | 0 | 0.4 | 0.0026787 | 0.0026787 | 0.17345
1320 | 36 | Pipe | 3 | 4.642 | 140 | 7.0686 | 9.4248 | 0.75 | 0.65671 | 0.054469 |  | 0 | 0.054469 | 0.22792
| 36 | 45 Deg Bend | 3 | 4.642 | 140 | 7.0686 | 9.4248 | 0.75 | 0.65671 | 0 | 0.4 | 0.0026787 | 0.0026787 | 0.2306
1320 | 36 | Pipe | 3 | 4.642 | 140 | 7.0686 | 9.4248 | 0.75 | 0.65671 | 0.054469 |  | 0 | 0.054469 | 0.28507
| 36 | 45 Deg Bend | 3 | 4.642 | 140 | 7.0686 | 9.4248 | 0.75 | 0.65671 | 0 | 0.4 | 0.0026787 | 0.0026787 | 0.28775
1320 | 36 | Pipe | 3 | 4.642 | 140 | 7.0686 | 9.4248 | 0.75 | 0.65671 | 0.054469 |  | 0 | 0.054469 | 0.34222
| 36 | 90 Deg Bend | 3 | 4.642 | 140 | 7.0686 | 9.4248 | 0.75 | 0.65671 | 0 | 0.2 | 0.0013393 | 0.0013393 | 0.34356
1320 | 36 | Pipe | 3 | 4.642 | 140 | 7.0686 | 9.4248 | 0.75 | 0.65671 | 0.054469 |  | 0 | 0.054469 | 0.39802
| 36 | Exit to Headworks | 3 | 4.642 | 140 | 7.0686 | 9.4248 | 0.75 | 0.65671 | 0 | 1 | 0.0066967 | 0.0066967 | 0.40472
[13 empty] | Total | 0.40472
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 3 | 4.642 | 100 | 7.0686 | 9.4248 | 0.75 | 0.65671 | 0 | 0.25 | 0.0016742 | 0.0016742 | 0.0016742
| 36 | 30" X 36" Increaser | 3 | 4.642 | 100 | 7.0686 | 9.4248 | 0.75 | 0.65671 | 0 | 0.25 | 0.0016742 | 0.0016742 | 0.0033483
1320 | 36 | Pipe | 3 | 4.642 | 100 | 7.0686 | 9.4248 | 0.75 | 0.65671 | 0.1015 |  | 0 | 0.1015 | 0.10485
| 36 | 90 Deg Bend | 3 | 4.642 | 100 | 7.0686 | 9.4248 | 0.75 | 0.65671 | 0 | 0.2 | 0.0013393 | 0.0013393 | 0.10619
1320 | 36 | Pipe | 3 | 4.642 | 100 | 7.0686 | 9.4248 | 0.75 | 0.65671 | 0.1015 |  | 0 | 0.1015 | 0.2077
| 36 | 45 Deg Bend | 3 | 4.642 | 100 | 7.0686 | 9.4248 | 0.75 | 0.65671 | 0 | 0.4 | 0.0026787 | 0.0026787 | 0.21038
1320 | 36 | Pipe | 3 | 4.642 | 100 | 7.0686 | 9.4248 | 0.75 | 0.65671 | 0.1015 |  | 0 | 0.1015 | 0.31188
| 36 | 45 Deg Bend | 3 | 4.642 | 100 | 7.0686 | 9.4248 | 0.75 | 0.65671 | 0 | 0.4 | 0.0026787 | 0.0026787 | 0.31456
1320 | 36 | Pipe | 3 | 4.642 | 100 | 7.0686 | 9.4248 | 0.75 | 0.65671 | 0.1015 |  | 0 | 0.1015 | 0.41606
| 36 | 45 Deg Bend | 3 | 4.642 | 100 | 7.0686 | 9.4248 | 0.75 | 0.65671 | 0 | 0.4 | 0.0026787 | 0.0026787 | 0.41874
1320 | 36 | Pipe | 3 | 4.642 | 100 | 7.0686 | 9.4248 | 0.75 | 0.65671 | 0.1015 |  | 0 | 0.1015 | 0.52025
| 36 | 45 Deg Bend | 3 | 4.642 | 100 | 7.0686 | 9.4248 | 0.75 | 0.65671 | 0 | 0.4 | 0.0026787 | 0.0026787 | 0.52293
1320 | 36 | Pipe | 3 | 4.642 | 100 | 7.0686 | 9.4248 | 0.75 | 0.65671 | 0.1015 |  | 0 | 0.1015 | 0.62443
| 36 | 90 Deg Bend | 3 | 4.642 | 100 | 7.0686 | 9.4248 | 0.75 | 0.65671 | 0 | 0.2 | 0.0013393 | 0.0013393 | 0.62577
1320 | 36 | Pipe | 3 | 4.642 | 100 | 7.0686 | 9.4248 | 0.75 | 0.65671 | 0.1015 |  | 0 | 0.1015 | 0.72727
| 36 | Exit to Headworks | 3 | 4.642 | 100 | 7.0686 | 9.4248 | 0.75 | 0.65671 | 0 | 1 | 0.0066967 | 0.0066967 | 0.73397
[13 empty] | Total | 0.73397

## HL 4.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 4 | 6.1893 | 140 | 7.0686 | 9.4248 | 0.75 | 0.87561 | 0 | 0.25 | 0.0029763 | 0.0029763 | 0.0029763
| 36 | 30" X 36" Increaser | 4 | 6.1893 | 140 | 7.0686 | 9.4248 | 0.75 | 0.87561 | 0 | 0.25 | 0.0029763 | 0.0029763 | 0.0059526
1320 | 36 | Pipe | 4 | 6.1893 | 140 | 7.0686 | 9.4248 | 0.75 | 0.87561 | 0.092744 |  | 0 | 0.092744 | 0.098697
| 36 | 90 Deg Bend | 4 | 6.1893 | 140 | 7.0686 | 9.4248 | 0.75 | 0.87561 | 0 | 0.2 | 0.002381 | 0.002381 | 0.10108
1320 | 36 | Pipe | 4 | 6.1893 | 140 | 7.0686 | 9.4248 | 0.75 | 0.87561 | 0.092744 |  | 0 | 0.092744 | 0.19382
| 36 | 45 Deg Bend | 4 | 6.1893 | 140 | 7.0686 | 9.4248 | 0.75 | 0.87561 | 0 | 0.4 | 0.0047621 | 0.0047621 | 0.19858
1320 | 36 | Pipe | 4 | 6.1893 | 140 | 7.0686 | 9.4248 | 0.75 | 0.87561 | 0.092744 |  | 0 | 0.092744 | 0.29133
| 36 | 45 Deg Bend | 4 | 6.1893 | 140 | 7.0686 | 9.4248 | 0.75 | 0.87561 | 0 | 0.4 | 0.0047621 | 0.0047621 | 0.29609
1320 | 36 | Pipe | 4 | 6.1893 | 140 | 7.0686 | 9.4248 | 0.75 | 0.87561 | 0.092744 |  | 0 | 0.092744 | 0.38883
| 36 | 45 Deg Bend | 4 | 6.1893 | 140 | 7.0686 | 9.4248 | 0.75 | 0.87561 | 0 | 0.4 | 0.0047621 | 0.0047621 | 0.3936
1320 | 36 | Pipe | 4 | 6.1893 | 140 | 7.0686 | 9.4248 | 0.75 | 0.87561 | 0.092744 |  | 0 | 0.092744 | 0.48634
| 36 | 45 Deg Bend | 4 | 6.1893 | 140 | 7.0686 | 9.4248 | 0.75 | 0.87561 | 0 | 0.4 | 0.0047621 | 0.0047621 | 0.4911
1320 | 36 | Pipe | 4 | 6.1893 | 140 | 7.0686 | 9.4248 | 0.75 | 0.87561 | 0.092744 |  | 0 | 0.092744 | 0.58385
| 36 | 90 Deg Bend | 4 | 6.1893 | 140 | 7.0686 | 9.4248 | 0.75 | 0.87561 | 0 | 0.2 | 0.002381 | 0.002381 | 0.58623
1320 | 36 | Pipe | 4 | 6.1893 | 140 | 7.0686 | 9.4248 | 0.75 | 0.87561 | 0.092744 |  | 0 | 0.092744 | 0.67897
| 36 | Exit to Headworks | 4 | 6.1893 | 140 | 7.0686 | 9.4248 | 0.75 | 0.87561 | 0 | 1 | 0.011905 | 0.011905 | 0.69088
[13 empty] | Total | 0.69088
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 4 | 6.1893 | 100 | 7.0686 | 9.4248 | 0.75 | 0.87561 | 0 | 0.25 | 0.0029763 | 0.0029763 | 0.0029763
| 36 | 30" X 36" Increaser | 4 | 6.1893 | 100 | 7.0686 | 9.4248 | 0.75 | 0.87561 | 0 | 0.25 | 0.0029763 | 0.0029763 | 0.0059526
1320 | 36 | Pipe | 4 | 6.1893 | 100 | 7.0686 | 9.4248 | 0.75 | 0.87561 | 0.17283 |  | 0 | 0.17283 | 0.17878
| 36 | 90 Deg Bend | 4 | 6.1893 | 100 | 7.0686 | 9.4248 | 0.75 | 0.87561 | 0 | 0.2 | 0.002381 | 0.002381 | 0.18116
1320 | 36 | Pipe | 4 | 6.1893 | 100 | 7.0686 | 9.4248 | 0.75 | 0.87561 | 0.17283 |  | 0 | 0.17283 | 0.354
| 36 | 45 Deg Bend | 4 | 6.1893 | 100 | 7.0686 | 9.4248 | 0.75 | 0.87561 | 0 | 0.4 | 0.0047621 | 0.0047621 | 0.35876
1320 | 36 | Pipe | 4 | 6.1893 | 100 | 7.0686 | 9.4248 | 0.75 | 0.87561 | 0.17283 |  | 0 | 0.17283 | 0.53159
| 36 | 45 Deg Bend | 4 | 6.1893 | 100 | 7.0686 | 9.4248 | 0.75 | 0.87561 | 0 | 0.4 | 0.0047621 | 0.0047621 | 0.53635
1320 | 36 | Pipe | 4 | 6.1893 | 100 | 7.0686 | 9.4248 | 0.75 | 0.87561 | 0.17283 |  | 0 | 0.17283 | 0.70918
| 36 | 45 Deg Bend | 4 | 6.1893 | 100 | 7.0686 | 9.4248 | 0.75 | 0.87561 | 0 | 0.4 | 0.0047621 | 0.0047621 | 0.71394
1320 | 36 | Pipe | 4 | 6.1893 | 100 | 7.0686 | 9.4248 | 0.75 | 0.87561 | 0.17283 |  | 0 | 0.17283 | 0.88678
| 36 | 45 Deg Bend | 4 | 6.1893 | 100 | 7.0686 | 9.4248 | 0.75 | 0.87561 | 0 | 0.4 | 0.0047621 | 0.0047621 | 0.89154
1320 | 36 | Pipe | 4 | 6.1893 | 100 | 7.0686 | 9.4248 | 0.75 | 0.87561 | 0.17283 |  | 0 | 0.17283 | 1.0644
| 36 | 90 Deg Bend | 4 | 6.1893 | 100 | 7.0686 | 9.4248 | 0.75 | 0.87561 | 0 | 0.2 | 0.002381 | 0.002381 | 1.0668
1320 | 36 | Pipe | 4 | 6.1893 | 100 | 7.0686 | 9.4248 | 0.75 | 0.87561 | 0.17283 |  | 0 | 0.17283 | 1.2396
| 36 | Exit to Headworks | 4 | 6.1893 | 100 | 7.0686 | 9.4248 | 0.75 | 0.87561 | 0 | 1 | 0.011905 | 0.011905 | 1.2515
[13 empty] | Total | 1.2515

## HL 5.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 5 | 7.7367 | 140 | 7.0686 | 9.4248 | 0.75 | 1.0945 | 0 | 0.25 | 0.0046505 | 0.0046505 | 0.0046505
| 36 | 30" X 36" Increaser | 5 | 7.7367 | 140 | 7.0686 | 9.4248 | 0.75 | 1.0945 | 0 | 0.25 | 0.0046505 | 0.0046505 | 0.0093009
1320 | 36 | Pipe | 5 | 7.7367 | 140 | 7.0686 | 9.4248 | 0.75 | 1.0945 | 0.14014 |  | 0 | 0.14014 | 0.14944
| 36 | 90 Deg Bend | 5 | 7.7367 | 140 | 7.0686 | 9.4248 | 0.75 | 1.0945 | 0 | 0.2 | 0.0037204 | 0.0037204 | 0.15316
1320 | 36 | Pipe | 5 | 7.7367 | 140 | 7.0686 | 9.4248 | 0.75 | 1.0945 | 0.14014 |  | 0 | 0.14014 | 0.29331
| 36 | 45 Deg Bend | 5 | 7.7367 | 140 | 7.0686 | 9.4248 | 0.75 | 1.0945 | 0 | 0.4 | 0.0074407 | 0.0074407 | 0.30075
1320 | 36 | Pipe | 5 | 7.7367 | 140 | 7.0686 | 9.4248 | 0.75 | 1.0945 | 0.14014 |  | 0 | 0.14014 | 0.44089
| 36 | 45 Deg Bend | 5 | 7.7367 | 140 | 7.0686 | 9.4248 | 0.75 | 1.0945 | 0 | 0.4 | 0.0074407 | 0.0074407 | 0.44833
1320 | 36 | Pipe | 5 | 7.7367 | 140 | 7.0686 | 9.4248 | 0.75 | 1.0945 | 0.14014 |  | 0 | 0.14014 | 0.58847
| 36 | 45 Deg Bend | 5 | 7.7367 | 140 | 7.0686 | 9.4248 | 0.75 | 1.0945 | 0 | 0.4 | 0.0074407 | 0.0074407 | 0.59591
1320 | 36 | Pipe | 5 | 7.7367 | 140 | 7.0686 | 9.4248 | 0.75 | 1.0945 | 0.14014 |  | 0 | 0.14014 | 0.73605
| 36 | 45 Deg Bend | 5 | 7.7367 | 140 | 7.0686 | 9.4248 | 0.75 | 1.0945 | 0 | 0.4 | 0.0074407 | 0.0074407 | 0.7435
1320 | 36 | Pipe | 5 | 7.7367 | 140 | 7.0686 | 9.4248 | 0.75 | 1.0945 | 0.14014 |  | 0 | 0.14014 | 0.88364
| 36 | 90 Deg Bend | 5 | 7.7367 | 140 | 7.0686 | 9.4248 | 0.75 | 1.0945 | 0 | 0.2 | 0.0037204 | 0.0037204 | 0.88736
1320 | 36 | Pipe | 5 | 7.7367 | 140 | 7.0686 | 9.4248 | 0.75 | 1.0945 | 0.14014 |  | 0 | 0.14014 | 1.0275
| 36 | Exit to Headworks | 5 | 7.7367 | 140 | 7.0686 | 9.4248 | 0.75 | 1.0945 | 0 | 1 | 0.018602 | 0.018602 | 1.0461
[13 empty] | Total | 1.0461
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 5 | 7.7367 | 100 | 7.0686 | 9.4248 | 0.75 | 1.0945 | 0 | 0.25 | 0.0046505 | 0.0046505 | 0.0046505
| 36 | 30" X 36" Increaser | 5 | 7.7367 | 100 | 7.0686 | 9.4248 | 0.75 | 1.0945 | 0 | 0.25 | 0.0046505 | 0.0046505 | 0.0093009
1320 | 36 | Pipe | 5 | 7.7367 | 100 | 7.0686 | 9.4248 | 0.75 | 1.0945 | 0.26116 |  | 0 | 0.26116 | 0.27046
| 36 | 90 Deg Bend | 5 | 7.7367 | 100 | 7.0686 | 9.4248 | 0.75 | 1.0945 | 0 | 0.2 | 0.0037204 | 0.0037204 | 0.27418
1320 | 36 | Pipe | 5 | 7.7367 | 100 | 7.0686 | 9.4248 | 0.75 | 1.0945 | 0.26116 |  | 0 | 0.26116 | 0.53534
| 36 | 45 Deg Bend | 5 | 7.7367 | 100 | 7.0686 | 9.4248 | 0.75 | 1.0945 | 0 | 0.4 | 0.0074407 | 0.0074407 | 0.54278
1320 | 36 | Pipe | 5 | 7.7367 | 100 | 7.0686 | 9.4248 | 0.75 | 1.0945 | 0.26116 |  | 0 | 0.26116 | 0.80394
| 36 | 45 Deg Bend | 5 | 7.7367 | 100 | 7.0686 | 9.4248 | 0.75 | 1.0945 | 0 | 0.4 | 0.0074407 | 0.0074407 | 0.81138
1320 | 36 | Pipe | 5 | 7.7367 | 100 | 7.0686 | 9.4248 | 0.75 | 1.0945 | 0.26116 |  | 0 | 0.26116 | 1.0725
| 36 | 45 Deg Bend | 5 | 7.7367 | 100 | 7.0686 | 9.4248 | 0.75 | 1.0945 | 0 | 0.4 | 0.0074407 | 0.0074407 | 1.08
1320 | 36 | Pipe | 5 | 7.7367 | 100 | 7.0686 | 9.4248 | 0.75 | 1.0945 | 0.26116 |  | 0 | 0.26116 | 1.3411
| 36 | 45 Deg Bend | 5 | 7.7367 | 100 | 7.0686 | 9.4248 | 0.75 | 1.0945 | 0 | 0.4 | 0.0074407 | 0.0074407 | 1.3486
1320 | 36 | Pipe | 5 | 7.7367 | 100 | 7.0686 | 9.4248 | 0.75 | 1.0945 | 0.26116 |  | 0 | 0.26116 | 1.6097
| 36 | 90 Deg Bend | 5 | 7.7367 | 100 | 7.0686 | 9.4248 | 0.75 | 1.0945 | 0 | 0.2 | 0.0037204 | 0.0037204 | 1.6135
1320 | 36 | Pipe | 5 | 7.7367 | 100 | 7.0686 | 9.4248 | 0.75 | 1.0945 | 0.26116 |  | 0 | 0.26116 | 1.8746
| 36 | Exit to Headworks | 5 | 7.7367 | 100 | 7.0686 | 9.4248 | 0.75 | 1.0945 | 0 | 1 | 0.018602 | 0.018602 | 1.8932
[13 empty] | Total | 1.8932

## HL 6.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 6 | 9.284 | 140 | 7.0686 | 9.4248 | 0.75 | 1.3134 | 0 | 0.25 | 0.0066967 | 0.0066967 | 0.0066967
| 36 | 30" X 36" Increaser | 6 | 9.284 | 140 | 7.0686 | 9.4248 | 0.75 | 1.3134 | 0 | 0.25 | 0.0066967 | 0.0066967 | 0.013393
1320 | 36 | Pipe | 6 | 9.284 | 140 | 7.0686 | 9.4248 | 0.75 | 1.3134 | 0.19636 |  | 0 | 0.19636 | 0.20975
| 36 | 90 Deg Bend | 6 | 9.284 | 140 | 7.0686 | 9.4248 | 0.75 | 1.3134 | 0 | 0.2 | 0.0053573 | 0.0053573 | 0.21511
1320 | 36 | Pipe | 6 | 9.284 | 140 | 7.0686 | 9.4248 | 0.75 | 1.3134 | 0.19636 |  | 0 | 0.19636 | 0.41147
| 36 | 45 Deg Bend | 6 | 9.284 | 140 | 7.0686 | 9.4248 | 0.75 | 1.3134 | 0 | 0.4 | 0.010715 | 0.010715 | 0.42219
1320 | 36 | Pipe | 6 | 9.284 | 140 | 7.0686 | 9.4248 | 0.75 | 1.3134 | 0.19636 |  | 0 | 0.19636 | 0.61855
| 36 | 45 Deg Bend | 6 | 9.284 | 140 | 7.0686 | 9.4248 | 0.75 | 1.3134 | 0 | 0.4 | 0.010715 | 0.010715 | 0.62926
1320 | 36 | Pipe | 6 | 9.284 | 140 | 7.0686 | 9.4248 | 0.75 | 1.3134 | 0.19636 |  | 0 | 0.19636 | 0.82562
| 36 | 45 Deg Bend | 6 | 9.284 | 140 | 7.0686 | 9.4248 | 0.75 | 1.3134 | 0 | 0.4 | 0.010715 | 0.010715 | 0.83634
1320 | 36 | Pipe | 6 | 9.284 | 140 | 7.0686 | 9.4248 | 0.75 | 1.3134 | 0.19636 |  | 0 | 0.19636 | 1.0327
| 36 | 45 Deg Bend | 6 | 9.284 | 140 | 7.0686 | 9.4248 | 0.75 | 1.3134 | 0 | 0.4 | 0.010715 | 0.010715 | 1.0434
1320 | 36 | Pipe | 6 | 9.284 | 140 | 7.0686 | 9.4248 | 0.75 | 1.3134 | 0.19636 |  | 0 | 0.19636 | 1.2398
| 36 | 90 Deg Bend | 6 | 9.284 | 140 | 7.0686 | 9.4248 | 0.75 | 1.3134 | 0 | 0.2 | 0.0053573 | 0.0053573 | 1.2451
1320 | 36 | Pipe | 6 | 9.284 | 140 | 7.0686 | 9.4248 | 0.75 | 1.3134 | 0.19636 |  | 0 | 0.19636 | 1.4415
| 36 | Exit to Headworks | 6 | 9.284 | 140 | 7.0686 | 9.4248 | 0.75 | 1.3134 | 0 | 1 | 0.026787 | 0.026787 | 1.4683
[13 empty] | Total | 1.4683
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 6 | 9.284 | 100 | 7.0686 | 9.4248 | 0.75 | 1.3134 | 0 | 0.25 | 0.0066967 | 0.0066967 | 0.0066967
| 36 | 30" X 36" Increaser | 6 | 9.284 | 100 | 7.0686 | 9.4248 | 0.75 | 1.3134 | 0 | 0.25 | 0.0066967 | 0.0066967 | 0.013393
1320 | 36 | Pipe | 6 | 9.284 | 100 | 7.0686 | 9.4248 | 0.75 | 1.3134 | 0.36592 |  | 0 | 0.36592 | 0.37932
| 36 | 90 Deg Bend | 6 | 9.284 | 100 | 7.0686 | 9.4248 | 0.75 | 1.3134 | 0 | 0.2 | 0.0053573 | 0.0053573 | 0.38467
1320 | 36 | Pipe | 6 | 9.284 | 100 | 7.0686 | 9.4248 | 0.75 | 1.3134 | 0.36592 |  | 0 | 0.36592 | 0.7506
| 36 | 45 Deg Bend | 6 | 9.284 | 100 | 7.0686 | 9.4248 | 0.75 | 1.3134 | 0 | 0.4 | 0.010715 | 0.010715 | 0.76131
1320 | 36 | Pipe | 6 | 9.284 | 100 | 7.0686 | 9.4248 | 0.75 | 1.3134 | 0.36592 |  | 0 | 0.36592 | 1.1272
| 36 | 45 Deg Bend | 6 | 9.284 | 100 | 7.0686 | 9.4248 | 0.75 | 1.3134 | 0 | 0.4 | 0.010715 | 0.010715 | 1.138
1320 | 36 | Pipe | 6 | 9.284 | 100 | 7.0686 | 9.4248 | 0.75 | 1.3134 | 0.36592 |  | 0 | 0.36592 | 1.5039
| 36 | 45 Deg Bend | 6 | 9.284 | 100 | 7.0686 | 9.4248 | 0.75 | 1.3134 | 0 | 0.4 | 0.010715 | 0.010715 | 1.5146
1320 | 36 | Pipe | 6 | 9.284 | 100 | 7.0686 | 9.4248 | 0.75 | 1.3134 | 0.36592 |  | 0 | 0.36592 | 1.8805
| 36 | 45 Deg Bend | 6 | 9.284 | 100 | 7.0686 | 9.4248 | 0.75 | 1.3134 | 0 | 0.4 | 0.010715 | 0.010715 | 1.8912
1320 | 36 | Pipe | 6 | 9.284 | 100 | 7.0686 | 9.4248 | 0.75 | 1.3134 | 0.36592 |  | 0 | 0.36592 | 2.2572
| 36 | 90 Deg Bend | 6 | 9.284 | 100 | 7.0686 | 9.4248 | 0.75 | 1.3134 | 0 | 0.2 | 0.0053573 | 0.0053573 | 2.2625
1320 | 36 | Pipe | 6 | 9.284 | 100 | 7.0686 | 9.4248 | 0.75 | 1.3134 | 0.36592 |  | 0 | 0.36592 | 2.6284
| 36 | Exit to Headworks | 6 | 9.284 | 100 | 7.0686 | 9.4248 | 0.75 | 1.3134 | 0 | 1 | 0.026787 | 0.026787 | 2.6552
[13 empty] | Total | 2.6552

## HL 7.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 7 | 10.8314 | 140 | 7.0686 | 9.4248 | 0.75 | 1.5323 | 0 | 0.25 | 0.0091149 | 0.0091149 | 0.0091149
| 36 | 30" X 36" Increaser | 7 | 10.8314 | 140 | 7.0686 | 9.4248 | 0.75 | 1.5323 | 0 | 0.25 | 0.0091149 | 0.0091149 | 0.01823
1320 | 36 | Pipe | 7 | 10.8314 | 140 | 7.0686 | 9.4248 | 0.75 | 1.5323 | 0.26116 |  | 0 | 0.26116 | 0.27939
| 36 | 90 Deg Bend | 7 | 10.8314 | 140 | 7.0686 | 9.4248 | 0.75 | 1.5323 | 0 | 0.2 | 0.0072919 | 0.0072919 | 0.28668
1320 | 36 | Pipe | 7 | 10.8314 | 140 | 7.0686 | 9.4248 | 0.75 | 1.5323 | 0.26116 |  | 0 | 0.26116 | 0.54784
| 36 | 45 Deg Bend | 7 | 10.8314 | 140 | 7.0686 | 9.4248 | 0.75 | 1.5323 | 0 | 0.4 | 0.014584 | 0.014584 | 0.56242
1320 | 36 | Pipe | 7 | 10.8314 | 140 | 7.0686 | 9.4248 | 0.75 | 1.5323 | 0.26116 |  | 0 | 0.26116 | 0.82358
| 36 | 45 Deg Bend | 7 | 10.8314 | 140 | 7.0686 | 9.4248 | 0.75 | 1.5323 | 0 | 0.4 | 0.014584 | 0.014584 | 0.83817
1320 | 36 | Pipe | 7 | 10.8314 | 140 | 7.0686 | 9.4248 | 0.75 | 1.5323 | 0.26116 |  | 0 | 0.26116 | 1.0993
| 36 | 45 Deg Bend | 7 | 10.8314 | 140 | 7.0686 | 9.4248 | 0.75 | 1.5323 | 0 | 0.4 | 0.014584 | 0.014584 | 1.1139
1320 | 36 | Pipe | 7 | 10.8314 | 140 | 7.0686 | 9.4248 | 0.75 | 1.5323 | 0.26116 |  | 0 | 0.26116 | 1.3751
| 36 | 45 Deg Bend | 7 | 10.8314 | 140 | 7.0686 | 9.4248 | 0.75 | 1.5323 | 0 | 0.4 | 0.014584 | 0.014584 | 1.3897
1320 | 36 | Pipe | 7 | 10.8314 | 140 | 7.0686 | 9.4248 | 0.75 | 1.5323 | 0.26116 |  | 0 | 0.26116 | 1.6508
| 36 | 90 Deg Bend | 7 | 10.8314 | 140 | 7.0686 | 9.4248 | 0.75 | 1.5323 | 0 | 0.2 | 0.0072919 | 0.0072919 | 1.6581
1320 | 36 | Pipe | 7 | 10.8314 | 140 | 7.0686 | 9.4248 | 0.75 | 1.5323 | 0.26116 |  | 0 | 0.26116 | 1.9193
| 36 | Exit to Headworks | 7 | 10.8314 | 140 | 7.0686 | 9.4248 | 0.75 | 1.5323 | 0 | 1 | 0.03646 | 0.03646 | 1.9557
[13 empty] | Total | 1.9557
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 7 | 10.8314 | 100 | 7.0686 | 9.4248 | 0.75 | 1.5323 | 0 | 0.25 | 0.0091149 | 0.0091149 | 0.0091149
| 36 | 30" X 36" Increaser | 7 | 10.8314 | 100 | 7.0686 | 9.4248 | 0.75 | 1.5323 | 0 | 0.25 | 0.0091149 | 0.0091149 | 0.01823
1320 | 36 | Pipe | 7 | 10.8314 | 100 | 7.0686 | 9.4248 | 0.75 | 1.5323 | 0.48668 |  | 0 | 0.48668 | 0.50491
| 36 | 90 Deg Bend | 7 | 10.8314 | 100 | 7.0686 | 9.4248 | 0.75 | 1.5323 | 0 | 0.2 | 0.0072919 | 0.0072919 | 0.5122
1320 | 36 | Pipe | 7 | 10.8314 | 100 | 7.0686 | 9.4248 | 0.75 | 1.5323 | 0.48668 |  | 0 | 0.48668 | 0.99888
| 36 | 45 Deg Bend | 7 | 10.8314 | 100 | 7.0686 | 9.4248 | 0.75 | 1.5323 | 0 | 0.4 | 0.014584 | 0.014584 | 1.0135
1320 | 36 | Pipe | 7 | 10.8314 | 100 | 7.0686 | 9.4248 | 0.75 | 1.5323 | 0.48668 |  | 0 | 0.48668 | 1.5001
| 36 | 45 Deg Bend | 7 | 10.8314 | 100 | 7.0686 | 9.4248 | 0.75 | 1.5323 | 0 | 0.4 | 0.014584 | 0.014584 | 1.5147
1320 | 36 | Pipe | 7 | 10.8314 | 100 | 7.0686 | 9.4248 | 0.75 | 1.5323 | 0.48668 |  | 0 | 0.48668 | 2.0014
| 36 | 45 Deg Bend | 7 | 10.8314 | 100 | 7.0686 | 9.4248 | 0.75 | 1.5323 | 0 | 0.4 | 0.014584 | 0.014584 | 2.016
1320 | 36 | Pipe | 7 | 10.8314 | 100 | 7.0686 | 9.4248 | 0.75 | 1.5323 | 0.48668 |  | 0 | 0.48668 | 2.5027
| 36 | 45 Deg Bend | 7 | 10.8314 | 100 | 7.0686 | 9.4248 | 0.75 | 1.5323 | 0 | 0.4 | 0.014584 | 0.014584 | 2.5173
1320 | 36 | Pipe | 7 | 10.8314 | 100 | 7.0686 | 9.4248 | 0.75 | 1.5323 | 0.48668 |  | 0 | 0.48668 | 3.0039
| 36 | 90 Deg Bend | 7 | 10.8314 | 100 | 7.0686 | 9.4248 | 0.75 | 1.5323 | 0 | 0.2 | 0.0072919 | 0.0072919 | 3.0112
1320 | 36 | Pipe | 7 | 10.8314 | 100 | 7.0686 | 9.4248 | 0.75 | 1.5323 | 0.48668 |  | 0 | 0.48668 | 3.4979
| 36 | Exit to Headworks | 7 | 10.8314 | 100 | 7.0686 | 9.4248 | 0.75 | 1.5323 | 0 | 1 | 0.03646 | 0.03646 | 3.5344
[13 empty] | Total | 3.5344

## HL 8.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 8 | 12.3787 | 140 | 7.0686 | 9.4248 | 0.75 | 1.7512 | 0 | 0.25 | 0.011905 | 0.011905 | 0.011905
| 36 | 30" X 36" Increaser | 8 | 12.3787 | 140 | 7.0686 | 9.4248 | 0.75 | 1.7512 | 0 | 0.25 | 0.011905 | 0.011905 | 0.02381
1320 | 36 | Pipe | 8 | 12.3787 | 140 | 7.0686 | 9.4248 | 0.75 | 1.7512 | 0.33434 |  | 0 | 0.33434 | 0.35815
| 36 | 90 Deg Bend | 8 | 12.3787 | 140 | 7.0686 | 9.4248 | 0.75 | 1.7512 | 0 | 0.2 | 0.0095242 | 0.0095242 | 0.36768
1320 | 36 | Pipe | 8 | 12.3787 | 140 | 7.0686 | 9.4248 | 0.75 | 1.7512 | 0.33434 |  | 0 | 0.33434 | 0.70202
| 36 | 45 Deg Bend | 8 | 12.3787 | 140 | 7.0686 | 9.4248 | 0.75 | 1.7512 | 0 | 0.4 | 0.019048 | 0.019048 | 0.72107
1320 | 36 | Pipe | 8 | 12.3787 | 140 | 7.0686 | 9.4248 | 0.75 | 1.7512 | 0.33434 |  | 0 | 0.33434 | 1.0554
| 36 | 45 Deg Bend | 8 | 12.3787 | 140 | 7.0686 | 9.4248 | 0.75 | 1.7512 | 0 | 0.4 | 0.019048 | 0.019048 | 1.0745
1320 | 36 | Pipe | 8 | 12.3787 | 140 | 7.0686 | 9.4248 | 0.75 | 1.7512 | 0.33434 |  | 0 | 0.33434 | 1.4088
| 36 | 45 Deg Bend | 8 | 12.3787 | 140 | 7.0686 | 9.4248 | 0.75 | 1.7512 | 0 | 0.4 | 0.019048 | 0.019048 | 1.4278
1320 | 36 | Pipe | 8 | 12.3787 | 140 | 7.0686 | 9.4248 | 0.75 | 1.7512 | 0.33434 |  | 0 | 0.33434 | 1.7622
| 36 | 45 Deg Bend | 8 | 12.3787 | 140 | 7.0686 | 9.4248 | 0.75 | 1.7512 | 0 | 0.4 | 0.019048 | 0.019048 | 1.7812
1320 | 36 | Pipe | 8 | 12.3787 | 140 | 7.0686 | 9.4248 | 0.75 | 1.7512 | 0.33434 |  | 0 | 0.33434 | 2.1156
| 36 | 90 Deg Bend | 8 | 12.3787 | 140 | 7.0686 | 9.4248 | 0.75 | 1.7512 | 0 | 0.2 | 0.0095242 | 0.0095242 | 2.1251
1320 | 36 | Pipe | 8 | 12.3787 | 140 | 7.0686 | 9.4248 | 0.75 | 1.7512 | 0.33434 |  | 0 | 0.33434 | 2.4594
| 36 | Exit to Headworks | 8 | 12.3787 | 140 | 7.0686 | 9.4248 | 0.75 | 1.7512 | 0 | 1 | 0.047621 | 0.047621 | 2.5071
[13 empty] | Total | 2.5071
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 8 | 12.3787 | 100 | 7.0686 | 9.4248 | 0.75 | 1.7512 | 0 | 0.25 | 0.011905 | 0.011905 | 0.011905
| 36 | 30" X 36" Increaser | 8 | 12.3787 | 100 | 7.0686 | 9.4248 | 0.75 | 1.7512 | 0 | 0.25 | 0.011905 | 0.011905 | 0.02381
1320 | 36 | Pipe | 8 | 12.3787 | 100 | 7.0686 | 9.4248 | 0.75 | 1.7512 | 0.62306 |  | 0 | 0.62306 | 0.64687
| 36 | 90 Deg Bend | 8 | 12.3787 | 100 | 7.0686 | 9.4248 | 0.75 | 1.7512 | 0 | 0.2 | 0.0095242 | 0.0095242 | 0.65639
1320 | 36 | Pipe | 8 | 12.3787 | 100 | 7.0686 | 9.4248 | 0.75 | 1.7512 | 0.62306 |  | 0 | 0.62306 | 1.2794
| 36 | 45 Deg Bend | 8 | 12.3787 | 100 | 7.0686 | 9.4248 | 0.75 | 1.7512 | 0 | 0.4 | 0.019048 | 0.019048 | 1.2985
1320 | 36 | Pipe | 8 | 12.3787 | 100 | 7.0686 | 9.4248 | 0.75 | 1.7512 | 0.62306 |  | 0 | 0.62306 | 1.9216
| 36 | 45 Deg Bend | 8 | 12.3787 | 100 | 7.0686 | 9.4248 | 0.75 | 1.7512 | 0 | 0.4 | 0.019048 | 0.019048 | 1.9406
1320 | 36 | Pipe | 8 | 12.3787 | 100 | 7.0686 | 9.4248 | 0.75 | 1.7512 | 0.62306 |  | 0 | 0.62306 | 2.5637
| 36 | 45 Deg Bend | 8 | 12.3787 | 100 | 7.0686 | 9.4248 | 0.75 | 1.7512 | 0 | 0.4 | 0.019048 | 0.019048 | 2.5827
1320 | 36 | Pipe | 8 | 12.3787 | 100 | 7.0686 | 9.4248 | 0.75 | 1.7512 | 0.62306 |  | 0 | 0.62306 | 3.2058
| 36 | 45 Deg Bend | 8 | 12.3787 | 100 | 7.0686 | 9.4248 | 0.75 | 1.7512 | 0 | 0.4 | 0.019048 | 0.019048 | 3.2248
1320 | 36 | Pipe | 8 | 12.3787 | 100 | 7.0686 | 9.4248 | 0.75 | 1.7512 | 0.62306 |  | 0 | 0.62306 | 3.8479
| 36 | 90 Deg Bend | 8 | 12.3787 | 100 | 7.0686 | 9.4248 | 0.75 | 1.7512 | 0 | 0.2 | 0.0095242 | 0.0095242 | 3.8574
1320 | 36 | Pipe | 8 | 12.3787 | 100 | 7.0686 | 9.4248 | 0.75 | 1.7512 | 0.62306 |  | 0 | 0.62306 | 4.4805
| 36 | Exit to Headworks | 8 | 12.3787 | 100 | 7.0686 | 9.4248 | 0.75 | 1.7512 | 0 | 1 | 0.047621 | 0.047621 | 4.5281
[13 empty] | Total | 4.5281

## HL 9.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 9 | 13.926 | 140 | 7.0686 | 9.4248 | 0.75 | 1.9701 | 0 | 0.25 | 0.015068 | 0.015068 | 0.015068
| 36 | 30" X 36" Increaser | 9 | 13.926 | 140 | 7.0686 | 9.4248 | 0.75 | 1.9701 | 0 | 0.25 | 0.015068 | 0.015068 | 0.030135
1320 | 36 | Pipe | 9 | 13.926 | 140 | 7.0686 | 9.4248 | 0.75 | 1.9701 | 0.41574 |  | 0 | 0.41574 | 0.44588
| 36 | 90 Deg Bend | 9 | 13.926 | 140 | 7.0686 | 9.4248 | 0.75 | 1.9701 | 0 | 0.2 | 0.012054 | 0.012054 | 0.45793
1320 | 36 | Pipe | 9 | 13.926 | 140 | 7.0686 | 9.4248 | 0.75 | 1.9701 | 0.41574 |  | 0 | 0.41574 | 0.87367
| 36 | 45 Deg Bend | 9 | 13.926 | 140 | 7.0686 | 9.4248 | 0.75 | 1.9701 | 0 | 0.4 | 0.024108 | 0.024108 | 0.89778
1320 | 36 | Pipe | 9 | 13.926 | 140 | 7.0686 | 9.4248 | 0.75 | 1.9701 | 0.41574 |  | 0 | 0.41574 | 1.3135
| 36 | 45 Deg Bend | 9 | 13.926 | 140 | 7.0686 | 9.4248 | 0.75 | 1.9701 | 0 | 0.4 | 0.024108 | 0.024108 | 1.3376
1320 | 36 | Pipe | 9 | 13.926 | 140 | 7.0686 | 9.4248 | 0.75 | 1.9701 | 0.41574 |  | 0 | 0.41574 | 1.7534
| 36 | 45 Deg Bend | 9 | 13.926 | 140 | 7.0686 | 9.4248 | 0.75 | 1.9701 | 0 | 0.4 | 0.024108 | 0.024108 | 1.7775
1320 | 36 | Pipe | 9 | 13.926 | 140 | 7.0686 | 9.4248 | 0.75 | 1.9701 | 0.41574 |  | 0 | 0.41574 | 2.1932
| 36 | 45 Deg Bend | 9 | 13.926 | 140 | 7.0686 | 9.4248 | 0.75 | 1.9701 | 0 | 0.4 | 0.024108 | 0.024108 | 2.2173
1320 | 36 | Pipe | 9 | 13.926 | 140 | 7.0686 | 9.4248 | 0.75 | 1.9701 | 0.41574 |  | 0 | 0.41574 | 2.6331
| 36 | 90 Deg Bend | 9 | 13.926 | 140 | 7.0686 | 9.4248 | 0.75 | 1.9701 | 0 | 0.2 | 0.012054 | 0.012054 | 2.6451
1320 | 36 | Pipe | 9 | 13.926 | 140 | 7.0686 | 9.4248 | 0.75 | 1.9701 | 0.41574 |  | 0 | 0.41574 | 3.0609
| 36 | Exit to Headworks | 9 | 13.926 | 140 | 7.0686 | 9.4248 | 0.75 | 1.9701 | 0 | 1 | 0.06027 | 0.06027 | 3.1211
[13 empty] | Total | 3.1211
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 9 | 13.926 | 100 | 7.0686 | 9.4248 | 0.75 | 1.9701 | 0 | 0.25 | 0.015068 | 0.015068 | 0.015068
| 36 | 30" X 36" Increaser | 9 | 13.926 | 100 | 7.0686 | 9.4248 | 0.75 | 1.9701 | 0 | 0.25 | 0.015068 | 0.015068 | 0.030135
1320 | 36 | Pipe | 9 | 13.926 | 100 | 7.0686 | 9.4248 | 0.75 | 1.9701 | 0.77475 |  | 0 | 0.77475 | 0.80488
| 36 | 90 Deg Bend | 9 | 13.926 | 100 | 7.0686 | 9.4248 | 0.75 | 1.9701 | 0 | 0.2 | 0.012054 | 0.012054 | 0.81694
1320 | 36 | Pipe | 9 | 13.926 | 100 | 7.0686 | 9.4248 | 0.75 | 1.9701 | 0.77475 |  | 0 | 0.77475 | 1.5917
| 36 | 45 Deg Bend | 9 | 13.926 | 100 | 7.0686 | 9.4248 | 0.75 | 1.9701 | 0 | 0.4 | 0.024108 | 0.024108 | 1.6158
1320 | 36 | Pipe | 9 | 13.926 | 100 | 7.0686 | 9.4248 | 0.75 | 1.9701 | 0.77475 |  | 0 | 0.77475 | 2.3905
| 36 | 45 Deg Bend | 9 | 13.926 | 100 | 7.0686 | 9.4248 | 0.75 | 1.9701 | 0 | 0.4 | 0.024108 | 0.024108 | 2.4146
1320 | 36 | Pipe | 9 | 13.926 | 100 | 7.0686 | 9.4248 | 0.75 | 1.9701 | 0.77475 |  | 0 | 0.77475 | 3.1894
| 36 | 45 Deg Bend | 9 | 13.926 | 100 | 7.0686 | 9.4248 | 0.75 | 1.9701 | 0 | 0.4 | 0.024108 | 0.024108 | 3.2135
1320 | 36 | Pipe | 9 | 13.926 | 100 | 7.0686 | 9.4248 | 0.75 | 1.9701 | 0.77475 |  | 0 | 0.77475 | 3.9882
| 36 | 45 Deg Bend | 9 | 13.926 | 100 | 7.0686 | 9.4248 | 0.75 | 1.9701 | 0 | 0.4 | 0.024108 | 0.024108 | 4.0124
1320 | 36 | Pipe | 9 | 13.926 | 100 | 7.0686 | 9.4248 | 0.75 | 1.9701 | 0.77475 |  | 0 | 0.77475 | 4.7871
| 36 | 90 Deg Bend | 9 | 13.926 | 100 | 7.0686 | 9.4248 | 0.75 | 1.9701 | 0 | 0.2 | 0.012054 | 0.012054 | 4.7992
1320 | 36 | Pipe | 9 | 13.926 | 100 | 7.0686 | 9.4248 | 0.75 | 1.9701 | 0.77475 |  | 0 | 0.77475 | 5.5739
| 36 | Exit to Headworks | 9 | 13.926 | 100 | 7.0686 | 9.4248 | 0.75 | 1.9701 | 0 | 1 | 0.06027 | 0.06027 | 5.6342
[13 empty] | Total | 5.6342

## HL 10.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 10 | 15.4734 | 140 | 7.0686 | 9.4248 | 0.75 | 2.189 | 0 | 0.25 | 0.018602 | 0.018602 | 0.018602
| 36 | 30" X 36" Increaser | 10 | 15.4734 | 140 | 7.0686 | 9.4248 | 0.75 | 2.189 | 0 | 0.25 | 0.018602 | 0.018602 | 0.037204
1320 | 36 | Pipe | 10 | 15.4734 | 140 | 7.0686 | 9.4248 | 0.75 | 2.189 | 0.50521 |  | 0 | 0.50521 | 0.54242
| 36 | 90 Deg Bend | 10 | 15.4734 | 140 | 7.0686 | 9.4248 | 0.75 | 2.189 | 0 | 0.2 | 0.014881 | 0.014881 | 0.5573
1320 | 36 | Pipe | 10 | 15.4734 | 140 | 7.0686 | 9.4248 | 0.75 | 2.189 | 0.50521 |  | 0 | 0.50521 | 1.0625
| 36 | 45 Deg Bend | 10 | 15.4734 | 140 | 7.0686 | 9.4248 | 0.75 | 2.189 | 0 | 0.4 | 0.029763 | 0.029763 | 1.0923
1320 | 36 | Pipe | 10 | 15.4734 | 140 | 7.0686 | 9.4248 | 0.75 | 2.189 | 0.50521 |  | 0 | 0.50521 | 1.5975
| 36 | 45 Deg Bend | 10 | 15.4734 | 140 | 7.0686 | 9.4248 | 0.75 | 2.189 | 0 | 0.4 | 0.029763 | 0.029763 | 1.6273
1320 | 36 | Pipe | 10 | 15.4734 | 140 | 7.0686 | 9.4248 | 0.75 | 2.189 | 0.50521 |  | 0 | 0.50521 | 2.1325
| 36 | 45 Deg Bend | 10 | 15.4734 | 140 | 7.0686 | 9.4248 | 0.75 | 2.189 | 0 | 0.4 | 0.029763 | 0.029763 | 2.1622
1320 | 36 | Pipe | 10 | 15.4734 | 140 | 7.0686 | 9.4248 | 0.75 | 2.189 | 0.50521 |  | 0 | 0.50521 | 2.6674
| 36 | 45 Deg Bend | 10 | 15.4734 | 140 | 7.0686 | 9.4248 | 0.75 | 2.189 | 0 | 0.4 | 0.029763 | 0.029763 | 2.6972
1320 | 36 | Pipe | 10 | 15.4734 | 140 | 7.0686 | 9.4248 | 0.75 | 2.189 | 0.50521 |  | 0 | 0.50521 | 3.2024
| 36 | 90 Deg Bend | 10 | 15.4734 | 140 | 7.0686 | 9.4248 | 0.75 | 2.189 | 0 | 0.2 | 0.014881 | 0.014881 | 3.2173
1320 | 36 | Pipe | 10 | 15.4734 | 140 | 7.0686 | 9.4248 | 0.75 | 2.189 | 0.50521 |  | 0 | 0.50521 | 3.7225
| 36 | Exit to Headworks | 10 | 15.4734 | 140 | 7.0686 | 9.4248 | 0.75 | 2.189 | 0 | 1 | 0.074407 | 0.074407 | 3.7969
[13 empty] | Total | 3.7969
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 10 | 15.4734 | 100 | 7.0686 | 9.4248 | 0.75 | 2.189 | 0 | 0.25 | 0.018602 | 0.018602 | 0.018602
| 36 | 30" X 36" Increaser | 10 | 15.4734 | 100 | 7.0686 | 9.4248 | 0.75 | 2.189 | 0 | 0.25 | 0.018602 | 0.018602 | 0.037204
1320 | 36 | Pipe | 10 | 15.4734 | 100 | 7.0686 | 9.4248 | 0.75 | 2.189 | 0.94148 |  | 0 | 0.94148 | 0.97868
| 36 | 90 Deg Bend | 10 | 15.4734 | 100 | 7.0686 | 9.4248 | 0.75 | 2.189 | 0 | 0.2 | 0.014881 | 0.014881 | 0.99357
1320 | 36 | Pipe | 10 | 15.4734 | 100 | 7.0686 | 9.4248 | 0.75 | 2.189 | 0.94148 |  | 0 | 0.94148 | 1.935
| 36 | 45 Deg Bend | 10 | 15.4734 | 100 | 7.0686 | 9.4248 | 0.75 | 2.189 | 0 | 0.4 | 0.029763 | 0.029763 | 1.9648
1320 | 36 | Pipe | 10 | 15.4734 | 100 | 7.0686 | 9.4248 | 0.75 | 2.189 | 0.94148 |  | 0 | 0.94148 | 2.9063
| 36 | 45 Deg Bend | 10 | 15.4734 | 100 | 7.0686 | 9.4248 | 0.75 | 2.189 | 0 | 0.4 | 0.029763 | 0.029763 | 2.9361
1320 | 36 | Pipe | 10 | 15.4734 | 100 | 7.0686 | 9.4248 | 0.75 | 2.189 | 0.94148 |  | 0 | 0.94148 | 3.8775
| 36 | 45 Deg Bend | 10 | 15.4734 | 100 | 7.0686 | 9.4248 | 0.75 | 2.189 | 0 | 0.4 | 0.029763 | 0.029763 | 3.9073
1320 | 36 | Pipe | 10 | 15.4734 | 100 | 7.0686 | 9.4248 | 0.75 | 2.189 | 0.94148 |  | 0 | 0.94148 | 4.8488
| 36 | 45 Deg Bend | 10 | 15.4734 | 100 | 7.0686 | 9.4248 | 0.75 | 2.189 | 0 | 0.4 | 0.029763 | 0.029763 | 4.8785
1320 | 36 | Pipe | 10 | 15.4734 | 100 | 7.0686 | 9.4248 | 0.75 | 2.189 | 0.94148 |  | 0 | 0.94148 | 5.82
| 36 | 90 Deg Bend | 10 | 15.4734 | 100 | 7.0686 | 9.4248 | 0.75 | 2.189 | 0 | 0.2 | 0.014881 | 0.014881 | 5.8349
1320 | 36 | Pipe | 10 | 15.4734 | 100 | 7.0686 | 9.4248 | 0.75 | 2.189 | 0.94148 |  | 0 | 0.94148 | 6.7764
| 36 | Exit to Headworks | 10 | 15.4734 | 100 | 7.0686 | 9.4248 | 0.75 | 2.189 | 0 | 1 | 0.074407 | 0.074407 | 6.8508
[13 empty] | Total | 6.8508

## HL 11.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 11 | 17.0207 | 140 | 7.0686 | 9.4248 | 0.75 | 2.4079 | 0 | 0.25 | 0.022508 | 0.022508 | 0.022508
| 36 | 30" X 36" Increaser | 11 | 17.0207 | 140 | 7.0686 | 9.4248 | 0.75 | 2.4079 | 0 | 0.25 | 0.022508 | 0.022508 | 0.045017
1320 | 36 | Pipe | 11 | 17.0207 | 140 | 7.0686 | 9.4248 | 0.75 | 2.4079 | 0.60263 |  | 0 | 0.60263 | 0.64765
| 36 | 90 Deg Bend | 11 | 17.0207 | 140 | 7.0686 | 9.4248 | 0.75 | 2.4079 | 0 | 0.2 | 0.018007 | 0.018007 | 0.66565
1320 | 36 | Pipe | 11 | 17.0207 | 140 | 7.0686 | 9.4248 | 0.75 | 2.4079 | 0.60263 |  | 0 | 0.60263 | 1.2683
| 36 | 45 Deg Bend | 11 | 17.0207 | 140 | 7.0686 | 9.4248 | 0.75 | 2.4079 | 0 | 0.4 | 0.036013 | 0.036013 | 1.3043
1320 | 36 | Pipe | 11 | 17.0207 | 140 | 7.0686 | 9.4248 | 0.75 | 2.4079 | 0.60263 |  | 0 | 0.60263 | 1.9069
| 36 | 45 Deg Bend | 11 | 17.0207 | 140 | 7.0686 | 9.4248 | 0.75 | 2.4079 | 0 | 0.4 | 0.036013 | 0.036013 | 1.9429
1320 | 36 | Pipe | 11 | 17.0207 | 140 | 7.0686 | 9.4248 | 0.75 | 2.4079 | 0.60263 |  | 0 | 0.60263 | 2.5456
| 36 | 45 Deg Bend | 11 | 17.0207 | 140 | 7.0686 | 9.4248 | 0.75 | 2.4079 | 0 | 0.4 | 0.036013 | 0.036013 | 2.5816
1320 | 36 | Pipe | 11 | 17.0207 | 140 | 7.0686 | 9.4248 | 0.75 | 2.4079 | 0.60263 |  | 0 | 0.60263 | 3.1842
| 36 | 45 Deg Bend | 11 | 17.0207 | 140 | 7.0686 | 9.4248 | 0.75 | 2.4079 | 0 | 0.4 | 0.036013 | 0.036013 | 3.2202
1320 | 36 | Pipe | 11 | 17.0207 | 140 | 7.0686 | 9.4248 | 0.75 | 2.4079 | 0.60263 |  | 0 | 0.60263 | 3.8229
| 36 | 90 Deg Bend | 11 | 17.0207 | 140 | 7.0686 | 9.4248 | 0.75 | 2.4079 | 0 | 0.2 | 0.018007 | 0.018007 | 3.8409
1320 | 36 | Pipe | 11 | 17.0207 | 140 | 7.0686 | 9.4248 | 0.75 | 2.4079 | 0.60263 |  | 0 | 0.60263 | 4.4435
| 36 | Exit to Headworks | 11 | 17.0207 | 140 | 7.0686 | 9.4248 | 0.75 | 2.4079 | 0 | 1 | 0.090033 | 0.090033 | 4.5335
[13 empty] | Total | 4.5335
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 11 | 17.0207 | 100 | 7.0686 | 9.4248 | 0.75 | 2.4079 | 0 | 0.25 | 0.022508 | 0.022508 | 0.022508
| 36 | 30" X 36" Increaser | 11 | 17.0207 | 100 | 7.0686 | 9.4248 | 0.75 | 2.4079 | 0 | 0.25 | 0.022508 | 0.022508 | 0.045017
1320 | 36 | Pipe | 11 | 17.0207 | 100 | 7.0686 | 9.4248 | 0.75 | 2.4079 | 1.123 |  | 0 | 1.123 | 1.168
| 36 | 90 Deg Bend | 11 | 17.0207 | 100 | 7.0686 | 9.4248 | 0.75 | 2.4079 | 0 | 0.2 | 0.018007 | 0.018007 | 1.186
1320 | 36 | Pipe | 11 | 17.0207 | 100 | 7.0686 | 9.4248 | 0.75 | 2.4079 | 1.123 |  | 0 | 1.123 | 2.3091
| 36 | 45 Deg Bend | 11 | 17.0207 | 100 | 7.0686 | 9.4248 | 0.75 | 2.4079 | 0 | 0.4 | 0.036013 | 0.036013 | 2.3451
1320 | 36 | Pipe | 11 | 17.0207 | 100 | 7.0686 | 9.4248 | 0.75 | 2.4079 | 1.123 |  | 0 | 1.123 | 3.4681
| 36 | 45 Deg Bend | 11 | 17.0207 | 100 | 7.0686 | 9.4248 | 0.75 | 2.4079 | 0 | 0.4 | 0.036013 | 0.036013 | 3.5041
1320 | 36 | Pipe | 11 | 17.0207 | 100 | 7.0686 | 9.4248 | 0.75 | 2.4079 | 1.123 |  | 0 | 1.123 | 4.6271
| 36 | 45 Deg Bend | 11 | 17.0207 | 100 | 7.0686 | 9.4248 | 0.75 | 2.4079 | 0 | 0.4 | 0.036013 | 0.036013 | 4.6631
1320 | 36 | Pipe | 11 | 17.0207 | 100 | 7.0686 | 9.4248 | 0.75 | 2.4079 | 1.123 |  | 0 | 1.123 | 5.7862
| 36 | 45 Deg Bend | 11 | 17.0207 | 100 | 7.0686 | 9.4248 | 0.75 | 2.4079 | 0 | 0.4 | 0.036013 | 0.036013 | 5.8222
1320 | 36 | Pipe | 11 | 17.0207 | 100 | 7.0686 | 9.4248 | 0.75 | 2.4079 | 1.123 |  | 0 | 1.123 | 6.9452
| 36 | 90 Deg Bend | 11 | 17.0207 | 100 | 7.0686 | 9.4248 | 0.75 | 2.4079 | 0 | 0.2 | 0.018007 | 0.018007 | 6.9632
1320 | 36 | Pipe | 11 | 17.0207 | 100 | 7.0686 | 9.4248 | 0.75 | 2.4079 | 1.123 |  | 0 | 1.123 | 8.0862
| 36 | Exit to Headworks | 11 | 17.0207 | 100 | 7.0686 | 9.4248 | 0.75 | 2.4079 | 0 | 1 | 0.090033 | 0.090033 | 8.1763
[13 empty] | Total | 8.1763

## HL 12.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 12 | 18.568 | 140 | 7.0686 | 9.4248 | 0.75 | 2.6268 | 0 | 0.25 | 0.026787 | 0.026787 | 0.026787
| 36 | 30" X 36" Increaser | 12 | 18.568 | 140 | 7.0686 | 9.4248 | 0.75 | 2.6268 | 0 | 0.25 | 0.026787 | 0.026787 | 0.053573
1320 | 36 | Pipe | 12 | 18.568 | 140 | 7.0686 | 9.4248 | 0.75 | 2.6268 | 0.70788 |  | 0 | 0.70788 | 0.76145
| 36 | 90 Deg Bend | 12 | 18.568 | 140 | 7.0686 | 9.4248 | 0.75 | 2.6268 | 0 | 0.2 | 0.021429 | 0.021429 | 0.78288
1320 | 36 | Pipe | 12 | 18.568 | 140 | 7.0686 | 9.4248 | 0.75 | 2.6268 | 0.70788 |  | 0 | 0.70788 | 1.4908
| 36 | 45 Deg Bend | 12 | 18.568 | 140 | 7.0686 | 9.4248 | 0.75 | 2.6268 | 0 | 0.4 | 0.042859 | 0.042859 | 1.5336
1320 | 36 | Pipe | 12 | 18.568 | 140 | 7.0686 | 9.4248 | 0.75 | 2.6268 | 0.70788 |  | 0 | 0.70788 | 2.2415
| 36 | 45 Deg Bend | 12 | 18.568 | 140 | 7.0686 | 9.4248 | 0.75 | 2.6268 | 0 | 0.4 | 0.042859 | 0.042859 | 2.2844
1320 | 36 | Pipe | 12 | 18.568 | 140 | 7.0686 | 9.4248 | 0.75 | 2.6268 | 0.70788 |  | 0 | 0.70788 | 2.9922
| 36 | 45 Deg Bend | 12 | 18.568 | 140 | 7.0686 | 9.4248 | 0.75 | 2.6268 | 0 | 0.4 | 0.042859 | 0.042859 | 3.0351
1320 | 36 | Pipe | 12 | 18.568 | 140 | 7.0686 | 9.4248 | 0.75 | 2.6268 | 0.70788 |  | 0 | 0.70788 | 3.743
| 36 | 45 Deg Bend | 12 | 18.568 | 140 | 7.0686 | 9.4248 | 0.75 | 2.6268 | 0 | 0.4 | 0.042859 | 0.042859 | 3.7858
1320 | 36 | Pipe | 12 | 18.568 | 140 | 7.0686 | 9.4248 | 0.75 | 2.6268 | 0.70788 |  | 0 | 0.70788 | 4.4937
| 36 | 90 Deg Bend | 12 | 18.568 | 140 | 7.0686 | 9.4248 | 0.75 | 2.6268 | 0 | 0.2 | 0.021429 | 0.021429 | 4.5151
1320 | 36 | Pipe | 12 | 18.568 | 140 | 7.0686 | 9.4248 | 0.75 | 2.6268 | 0.70788 |  | 0 | 0.70788 | 5.223
| 36 | Exit to Headworks | 12 | 18.568 | 140 | 7.0686 | 9.4248 | 0.75 | 2.6268 | 0 | 1 | 0.10715 | 0.10715 | 5.3302
[13 empty] | Total | 5.3302
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 12 | 18.568 | 100 | 7.0686 | 9.4248 | 0.75 | 2.6268 | 0 | 0.25 | 0.026787 | 0.026787 | 0.026787
| 36 | 30" X 36" Increaser | 12 | 18.568 | 100 | 7.0686 | 9.4248 | 0.75 | 2.6268 | 0 | 0.25 | 0.026787 | 0.026787 | 0.053573
1320 | 36 | Pipe | 12 | 18.568 | 100 | 7.0686 | 9.4248 | 0.75 | 2.6268 | 1.3192 |  | 0 | 1.3192 | 1.3727
| 36 | 90 Deg Bend | 12 | 18.568 | 100 | 7.0686 | 9.4248 | 0.75 | 2.6268 | 0 | 0.2 | 0.021429 | 0.021429 | 1.3942
1320 | 36 | Pipe | 12 | 18.568 | 100 | 7.0686 | 9.4248 | 0.75 | 2.6268 | 1.3192 |  | 0 | 1.3192 | 2.7133
| 36 | 45 Deg Bend | 12 | 18.568 | 100 | 7.0686 | 9.4248 | 0.75 | 2.6268 | 0 | 0.4 | 0.042859 | 0.042859 | 2.7562
1320 | 36 | Pipe | 12 | 18.568 | 100 | 7.0686 | 9.4248 | 0.75 | 2.6268 | 1.3192 |  | 0 | 1.3192 | 4.0753
| 36 | 45 Deg Bend | 12 | 18.568 | 100 | 7.0686 | 9.4248 | 0.75 | 2.6268 | 0 | 0.4 | 0.042859 | 0.042859 | 4.1182
1320 | 36 | Pipe | 12 | 18.568 | 100 | 7.0686 | 9.4248 | 0.75 | 2.6268 | 1.3192 |  | 0 | 1.3192 | 5.4374
| 36 | 45 Deg Bend | 12 | 18.568 | 100 | 7.0686 | 9.4248 | 0.75 | 2.6268 | 0 | 0.4 | 0.042859 | 0.042859 | 5.4802
1320 | 36 | Pipe | 12 | 18.568 | 100 | 7.0686 | 9.4248 | 0.75 | 2.6268 | 1.3192 |  | 0 | 1.3192 | 6.7994
| 36 | 45 Deg Bend | 12 | 18.568 | 100 | 7.0686 | 9.4248 | 0.75 | 2.6268 | 0 | 0.4 | 0.042859 | 0.042859 | 6.8422
1320 | 36 | Pipe | 12 | 18.568 | 100 | 7.0686 | 9.4248 | 0.75 | 2.6268 | 1.3192 |  | 0 | 1.3192 | 8.1614
| 36 | 90 Deg Bend | 12 | 18.568 | 100 | 7.0686 | 9.4248 | 0.75 | 2.6268 | 0 | 0.2 | 0.021429 | 0.021429 | 8.1828
1320 | 36 | Pipe | 12 | 18.568 | 100 | 7.0686 | 9.4248 | 0.75 | 2.6268 | 1.3192 |  | 0 | 1.3192 | 9.502
| 36 | Exit to Headworks | 12 | 18.568 | 100 | 7.0686 | 9.4248 | 0.75 | 2.6268 | 0 | 1 | 0.10715 | 0.10715 | 9.6091
[13 empty] | Total | 9.6091

## HL 13.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 13 | 20.1154 | 140 | 7.0686 | 9.4248 | 0.75 | 2.8457 | 0 | 0.25 | 0.031437 | 0.031437 | 0.031437
| 36 | 30" X 36" Increaser | 13 | 20.1154 | 140 | 7.0686 | 9.4248 | 0.75 | 2.8457 | 0 | 0.25 | 0.031437 | 0.031437 | 0.062874
1320 | 36 | Pipe | 13 | 20.1154 | 140 | 7.0686 | 9.4248 | 0.75 | 2.8457 | 0.82086 |  | 0 | 0.82086 | 0.88374
| 36 | 90 Deg Bend | 13 | 20.1154 | 140 | 7.0686 | 9.4248 | 0.75 | 2.8457 | 0 | 0.2 | 0.02515 | 0.02515 | 0.90889
1320 | 36 | Pipe | 13 | 20.1154 | 140 | 7.0686 | 9.4248 | 0.75 | 2.8457 | 0.82086 |  | 0 | 0.82086 | 1.7297
| 36 | 45 Deg Bend | 13 | 20.1154 | 140 | 7.0686 | 9.4248 | 0.75 | 2.8457 | 0 | 0.4 | 0.050299 | 0.050299 | 1.78
1320 | 36 | Pipe | 13 | 20.1154 | 140 | 7.0686 | 9.4248 | 0.75 | 2.8457 | 0.82086 |  | 0 | 0.82086 | 2.6009
| 36 | 45 Deg Bend | 13 | 20.1154 | 140 | 7.0686 | 9.4248 | 0.75 | 2.8457 | 0 | 0.4 | 0.050299 | 0.050299 | 2.6512
1320 | 36 | Pipe | 13 | 20.1154 | 140 | 7.0686 | 9.4248 | 0.75 | 2.8457 | 0.82086 |  | 0 | 0.82086 | 3.4721
| 36 | 45 Deg Bend | 13 | 20.1154 | 140 | 7.0686 | 9.4248 | 0.75 | 2.8457 | 0 | 0.4 | 0.050299 | 0.050299 | 3.5224
1320 | 36 | Pipe | 13 | 20.1154 | 140 | 7.0686 | 9.4248 | 0.75 | 2.8457 | 0.82086 |  | 0 | 0.82086 | 4.3432
| 36 | 45 Deg Bend | 13 | 20.1154 | 140 | 7.0686 | 9.4248 | 0.75 | 2.8457 | 0 | 0.4 | 0.050299 | 0.050299 | 4.3935
1320 | 36 | Pipe | 13 | 20.1154 | 140 | 7.0686 | 9.4248 | 0.75 | 2.8457 | 0.82086 |  | 0 | 0.82086 | 5.2144
| 36 | 90 Deg Bend | 13 | 20.1154 | 140 | 7.0686 | 9.4248 | 0.75 | 2.8457 | 0 | 0.2 | 0.02515 | 0.02515 | 5.2395
1320 | 36 | Pipe | 13 | 20.1154 | 140 | 7.0686 | 9.4248 | 0.75 | 2.8457 | 0.82086 |  | 0 | 0.82086 | 6.0604
| 36 | Exit to Headworks | 13 | 20.1154 | 140 | 7.0686 | 9.4248 | 0.75 | 2.8457 | 0 | 1 | 0.12575 | 0.12575 | 6.1861
[13 empty] | Total | 6.1861
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 13 | 20.1154 | 100 | 7.0686 | 9.4248 | 0.75 | 2.8457 | 0 | 0.25 | 0.031437 | 0.031437 | 0.031437
| 36 | 30" X 36" Increaser | 13 | 20.1154 | 100 | 7.0686 | 9.4248 | 0.75 | 2.8457 | 0 | 0.25 | 0.031437 | 0.031437 | 0.062874
1320 | 36 | Pipe | 13 | 20.1154 | 100 | 7.0686 | 9.4248 | 0.75 | 2.8457 | 1.5297 |  | 0 | 1.5297 | 1.5926
| 36 | 90 Deg Bend | 13 | 20.1154 | 100 | 7.0686 | 9.4248 | 0.75 | 2.8457 | 0 | 0.2 | 0.02515 | 0.02515 | 1.6177
1320 | 36 | Pipe | 13 | 20.1154 | 100 | 7.0686 | 9.4248 | 0.75 | 2.8457 | 1.5297 |  | 0 | 1.5297 | 3.1474
| 36 | 45 Deg Bend | 13 | 20.1154 | 100 | 7.0686 | 9.4248 | 0.75 | 2.8457 | 0 | 0.4 | 0.050299 | 0.050299 | 3.1977
1320 | 36 | Pipe | 13 | 20.1154 | 100 | 7.0686 | 9.4248 | 0.75 | 2.8457 | 1.5297 |  | 0 | 1.5297 | 4.7274
| 36 | 45 Deg Bend | 13 | 20.1154 | 100 | 7.0686 | 9.4248 | 0.75 | 2.8457 | 0 | 0.4 | 0.050299 | 0.050299 | 4.7777
1320 | 36 | Pipe | 13 | 20.1154 | 100 | 7.0686 | 9.4248 | 0.75 | 2.8457 | 1.5297 |  | 0 | 1.5297 | 6.3074
| 36 | 45 Deg Bend | 13 | 20.1154 | 100 | 7.0686 | 9.4248 | 0.75 | 2.8457 | 0 | 0.4 | 0.050299 | 0.050299 | 6.3577
1320 | 36 | Pipe | 13 | 20.1154 | 100 | 7.0686 | 9.4248 | 0.75 | 2.8457 | 1.5297 |  | 0 | 1.5297 | 7.8874
| 36 | 45 Deg Bend | 13 | 20.1154 | 100 | 7.0686 | 9.4248 | 0.75 | 2.8457 | 0 | 0.4 | 0.050299 | 0.050299 | 7.9377
1320 | 36 | Pipe | 13 | 20.1154 | 100 | 7.0686 | 9.4248 | 0.75 | 2.8457 | 1.5297 |  | 0 | 1.5297 | 9.4674
| 36 | 90 Deg Bend | 13 | 20.1154 | 100 | 7.0686 | 9.4248 | 0.75 | 2.8457 | 0 | 0.2 | 0.02515 | 0.02515 | 9.4926
1320 | 36 | Pipe | 13 | 20.1154 | 100 | 7.0686 | 9.4248 | 0.75 | 2.8457 | 1.5297 |  | 0 | 1.5297 | 11.0223
| 36 | Exit to Headworks | 13 | 20.1154 | 100 | 7.0686 | 9.4248 | 0.75 | 2.8457 | 0 | 1 | 0.12575 | 0.12575 | 11.148
[13 empty] | Total | 11.148

## HL 14.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 14 | 21.6627 | 140 | 7.0686 | 9.4248 | 0.75 | 3.0646 | 0 | 0.25 | 0.03646 | 0.03646 | 0.03646
| 36 | 30" X 36" Increaser | 14 | 21.6627 | 140 | 7.0686 | 9.4248 | 0.75 | 3.0646 | 0 | 0.25 | 0.03646 | 0.03646 | 0.072919
1320 | 36 | Pipe | 14 | 21.6627 | 140 | 7.0686 | 9.4248 | 0.75 | 3.0646 | 0.94148 |  | 0 | 0.94148 | 1.0144
| 36 | 90 Deg Bend | 14 | 21.6627 | 140 | 7.0686 | 9.4248 | 0.75 | 3.0646 | 0 | 0.2 | 0.029168 | 0.029168 | 1.0436
1320 | 36 | Pipe | 14 | 21.6627 | 140 | 7.0686 | 9.4248 | 0.75 | 3.0646 | 0.94148 |  | 0 | 0.94148 | 1.985
| 36 | 45 Deg Bend | 14 | 21.6627 | 140 | 7.0686 | 9.4248 | 0.75 | 3.0646 | 0 | 0.4 | 0.058335 | 0.058335 | 2.0434
1320 | 36 | Pipe | 14 | 21.6627 | 140 | 7.0686 | 9.4248 | 0.75 | 3.0646 | 0.94148 |  | 0 | 0.94148 | 2.9849
| 36 | 45 Deg Bend | 14 | 21.6627 | 140 | 7.0686 | 9.4248 | 0.75 | 3.0646 | 0 | 0.4 | 0.058335 | 0.058335 | 3.0432
1320 | 36 | Pipe | 14 | 21.6627 | 140 | 7.0686 | 9.4248 | 0.75 | 3.0646 | 0.94148 |  | 0 | 0.94148 | 3.9847
| 36 | 45 Deg Bend | 14 | 21.6627 | 140 | 7.0686 | 9.4248 | 0.75 | 3.0646 | 0 | 0.4 | 0.058335 | 0.058335 | 4.043
1320 | 36 | Pipe | 14 | 21.6627 | 140 | 7.0686 | 9.4248 | 0.75 | 3.0646 | 0.94148 |  | 0 | 0.94148 | 4.9845
| 36 | 45 Deg Bend | 14 | 21.6627 | 140 | 7.0686 | 9.4248 | 0.75 | 3.0646 | 0 | 0.4 | 0.058335 | 0.058335 | 5.0428
1320 | 36 | Pipe | 14 | 21.6627 | 140 | 7.0686 | 9.4248 | 0.75 | 3.0646 | 0.94148 |  | 0 | 0.94148 | 5.9843
| 36 | 90 Deg Bend | 14 | 21.6627 | 140 | 7.0686 | 9.4248 | 0.75 | 3.0646 | 0 | 0.2 | 0.029168 | 0.029168 | 6.0135
1320 | 36 | Pipe | 14 | 21.6627 | 140 | 7.0686 | 9.4248 | 0.75 | 3.0646 | 0.94148 |  | 0 | 0.94148 | 6.955
| 36 | Exit to Headworks | 14 | 21.6627 | 140 | 7.0686 | 9.4248 | 0.75 | 3.0646 | 0 | 1 | 0.14584 | 0.14584 | 7.1008
[13 empty] | Total | 7.1008
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 14 | 21.6627 | 100 | 7.0686 | 9.4248 | 0.75 | 3.0646 | 0 | 0.25 | 0.03646 | 0.03646 | 0.03646
| 36 | 30" X 36" Increaser | 14 | 21.6627 | 100 | 7.0686 | 9.4248 | 0.75 | 3.0646 | 0 | 0.25 | 0.03646 | 0.03646 | 0.072919
1320 | 36 | Pipe | 14 | 21.6627 | 100 | 7.0686 | 9.4248 | 0.75 | 3.0646 | 1.7545 |  | 0 | 1.7545 | 1.8274
| 36 | 90 Deg Bend | 14 | 21.6627 | 100 | 7.0686 | 9.4248 | 0.75 | 3.0646 | 0 | 0.2 | 0.029168 | 0.029168 | 1.8566
1320 | 36 | Pipe | 14 | 21.6627 | 100 | 7.0686 | 9.4248 | 0.75 | 3.0646 | 1.7545 |  | 0 | 1.7545 | 3.611
| 36 | 45 Deg Bend | 14 | 21.6627 | 100 | 7.0686 | 9.4248 | 0.75 | 3.0646 | 0 | 0.4 | 0.058335 | 0.058335 | 3.6694
1320 | 36 | Pipe | 14 | 21.6627 | 100 | 7.0686 | 9.4248 | 0.75 | 3.0646 | 1.7545 |  | 0 | 1.7545 | 5.4239
| 36 | 45 Deg Bend | 14 | 21.6627 | 100 | 7.0686 | 9.4248 | 0.75 | 3.0646 | 0 | 0.4 | 0.058335 | 0.058335 | 5.4822
1320 | 36 | Pipe | 14 | 21.6627 | 100 | 7.0686 | 9.4248 | 0.75 | 3.0646 | 1.7545 |  | 0 | 1.7545 | 7.2367
| 36 | 45 Deg Bend | 14 | 21.6627 | 100 | 7.0686 | 9.4248 | 0.75 | 3.0646 | 0 | 0.4 | 0.058335 | 0.058335 | 7.295
1320 | 36 | Pipe | 14 | 21.6627 | 100 | 7.0686 | 9.4248 | 0.75 | 3.0646 | 1.7545 |  | 0 | 1.7545 | 9.0495
| 36 | 45 Deg Bend | 14 | 21.6627 | 100 | 7.0686 | 9.4248 | 0.75 | 3.0646 | 0 | 0.4 | 0.058335 | 0.058335 | 9.1078
1320 | 36 | Pipe | 14 | 21.6627 | 100 | 7.0686 | 9.4248 | 0.75 | 3.0646 | 1.7545 |  | 0 | 1.7545 | 10.8623
| 36 | 90 Deg Bend | 14 | 21.6627 | 100 | 7.0686 | 9.4248 | 0.75 | 3.0646 | 0 | 0.2 | 0.029168 | 0.029168 | 10.8915
1320 | 36 | Pipe | 14 | 21.6627 | 100 | 7.0686 | 9.4248 | 0.75 | 3.0646 | 1.7545 |  | 0 | 1.7545 | 12.646
| 36 | Exit to Headworks | 14 | 21.6627 | 100 | 7.0686 | 9.4248 | 0.75 | 3.0646 | 0 | 1 | 0.14584 | 0.14584 | 12.7918
[13 empty] | Total | 12.7918

## HL 15.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 15 | 23.21 | 140 | 7.0686 | 9.4248 | 0.75 | 3.2835 | 0 | 0.25 | 0.041854 | 0.041854 | 0.041854
| 36 | 30" X 36" Increaser | 15 | 23.21 | 140 | 7.0686 | 9.4248 | 0.75 | 3.2835 | 0 | 0.25 | 0.041854 | 0.041854 | 0.083708
1320 | 36 | Pipe | 15 | 23.21 | 140 | 7.0686 | 9.4248 | 0.75 | 3.2835 | 1.0697 |  | 0 | 1.0697 | 1.1534
| 36 | 90 Deg Bend | 15 | 23.21 | 140 | 7.0686 | 9.4248 | 0.75 | 3.2835 | 0 | 0.2 | 0.033483 | 0.033483 | 1.1868
1320 | 36 | Pipe | 15 | 23.21 | 140 | 7.0686 | 9.4248 | 0.75 | 3.2835 | 1.0697 |  | 0 | 1.0697 | 2.2565
| 36 | 45 Deg Bend | 15 | 23.21 | 140 | 7.0686 | 9.4248 | 0.75 | 3.2835 | 0 | 0.4 | 0.066967 | 0.066967 | 2.3235
1320 | 36 | Pipe | 15 | 23.21 | 140 | 7.0686 | 9.4248 | 0.75 | 3.2835 | 1.0697 |  | 0 | 1.0697 | 3.3931
| 36 | 45 Deg Bend | 15 | 23.21 | 140 | 7.0686 | 9.4248 | 0.75 | 3.2835 | 0 | 0.4 | 0.066967 | 0.066967 | 3.4601
1320 | 36 | Pipe | 15 | 23.21 | 140 | 7.0686 | 9.4248 | 0.75 | 3.2835 | 1.0697 |  | 0 | 1.0697 | 4.5297
| 36 | 45 Deg Bend | 15 | 23.21 | 140 | 7.0686 | 9.4248 | 0.75 | 3.2835 | 0 | 0.4 | 0.066967 | 0.066967 | 4.5967
1320 | 36 | Pipe | 15 | 23.21 | 140 | 7.0686 | 9.4248 | 0.75 | 3.2835 | 1.0697 |  | 0 | 1.0697 | 5.6664
| 36 | 45 Deg Bend | 15 | 23.21 | 140 | 7.0686 | 9.4248 | 0.75 | 3.2835 | 0 | 0.4 | 0.066967 | 0.066967 | 5.7333
1320 | 36 | Pipe | 15 | 23.21 | 140 | 7.0686 | 9.4248 | 0.75 | 3.2835 | 1.0697 |  | 0 | 1.0697 | 6.803
| 36 | 90 Deg Bend | 15 | 23.21 | 140 | 7.0686 | 9.4248 | 0.75 | 3.2835 | 0 | 0.2 | 0.033483 | 0.033483 | 6.8365
1320 | 36 | Pipe | 15 | 23.21 | 140 | 7.0686 | 9.4248 | 0.75 | 3.2835 | 1.0697 |  | 0 | 1.0697 | 7.9061
| 36 | Exit to Headworks | 15 | 23.21 | 140 | 7.0686 | 9.4248 | 0.75 | 3.2835 | 0 | 1 | 0.16742 | 0.16742 | 8.0735
[13 empty] | Total | 8.0735
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 15 | 23.21 | 100 | 7.0686 | 9.4248 | 0.75 | 3.2835 | 0 | 0.25 | 0.041854 | 0.041854 | 0.041854
| 36 | 30" X 36" Increaser | 15 | 23.21 | 100 | 7.0686 | 9.4248 | 0.75 | 3.2835 | 0 | 0.25 | 0.041854 | 0.041854 | 0.083708
1320 | 36 | Pipe | 15 | 23.21 | 100 | 7.0686 | 9.4248 | 0.75 | 3.2835 | 1.9933 |  | 0 | 1.9933 | 2.077
| 36 | 90 Deg Bend | 15 | 23.21 | 100 | 7.0686 | 9.4248 | 0.75 | 3.2835 | 0 | 0.2 | 0.033483 | 0.033483 | 2.1105
1320 | 36 | Pipe | 15 | 23.21 | 100 | 7.0686 | 9.4248 | 0.75 | 3.2835 | 1.9933 |  | 0 | 1.9933 | 4.1039
| 36 | 45 Deg Bend | 15 | 23.21 | 100 | 7.0686 | 9.4248 | 0.75 | 3.2835 | 0 | 0.4 | 0.066967 | 0.066967 | 4.1708
1320 | 36 | Pipe | 15 | 23.21 | 100 | 7.0686 | 9.4248 | 0.75 | 3.2835 | 1.9933 |  | 0 | 1.9933 | 6.1642
| 36 | 45 Deg Bend | 15 | 23.21 | 100 | 7.0686 | 9.4248 | 0.75 | 3.2835 | 0 | 0.4 | 0.066967 | 0.066967 | 6.2311
1320 | 36 | Pipe | 15 | 23.21 | 100 | 7.0686 | 9.4248 | 0.75 | 3.2835 | 1.9933 |  | 0 | 1.9933 | 8.2245
| 36 | 45 Deg Bend | 15 | 23.21 | 100 | 7.0686 | 9.4248 | 0.75 | 3.2835 | 0 | 0.4 | 0.066967 | 0.066967 | 8.2914
1320 | 36 | Pipe | 15 | 23.21 | 100 | 7.0686 | 9.4248 | 0.75 | 3.2835 | 1.9933 |  | 0 | 1.9933 | 10.2848
| 36 | 45 Deg Bend | 15 | 23.21 | 100 | 7.0686 | 9.4248 | 0.75 | 3.2835 | 0 | 0.4 | 0.066967 | 0.066967 | 10.3517
1320 | 36 | Pipe | 15 | 23.21 | 100 | 7.0686 | 9.4248 | 0.75 | 3.2835 | 1.9933 |  | 0 | 1.9933 | 12.3451
| 36 | 90 Deg Bend | 15 | 23.21 | 100 | 7.0686 | 9.4248 | 0.75 | 3.2835 | 0 | 0.2 | 0.033483 | 0.033483 | 12.3785
1320 | 36 | Pipe | 15 | 23.21 | 100 | 7.0686 | 9.4248 | 0.75 | 3.2835 | 1.9933 |  | 0 | 1.9933 | 14.3719
| 36 | Exit to Headworks | 15 | 23.21 | 100 | 7.0686 | 9.4248 | 0.75 | 3.2835 | 0 | 1 | 0.16742 | 0.16742 | 14.5393
[13 empty] | Total | 14.5393

## HL 16.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 16 | 24.7574 | 140 | 7.0686 | 9.4248 | 0.75 | 3.5024 | 0 | 0.25 | 0.047621 | 0.047621 | 0.047621
| 36 | 30" X 36" Increaser | 16 | 24.7574 | 140 | 7.0686 | 9.4248 | 0.75 | 3.5024 | 0 | 0.25 | 0.047621 | 0.047621 | 0.095242
1320 | 36 | Pipe | 16 | 24.7574 | 140 | 7.0686 | 9.4248 | 0.75 | 3.5024 | 1.2053 |  | 0 | 1.2053 | 1.3005
| 36 | 90 Deg Bend | 16 | 24.7574 | 140 | 7.0686 | 9.4248 | 0.75 | 3.5024 | 0 | 0.2 | 0.038097 | 0.038097 | 1.3386
1320 | 36 | Pipe | 16 | 24.7574 | 140 | 7.0686 | 9.4248 | 0.75 | 3.5024 | 1.2053 |  | 0 | 1.2053 | 2.5439
| 36 | 45 Deg Bend | 16 | 24.7574 | 140 | 7.0686 | 9.4248 | 0.75 | 3.5024 | 0 | 0.4 | 0.076193 | 0.076193 | 2.6201
1320 | 36 | Pipe | 16 | 24.7574 | 140 | 7.0686 | 9.4248 | 0.75 | 3.5024 | 1.2053 |  | 0 | 1.2053 | 3.8254
| 36 | 45 Deg Bend | 16 | 24.7574 | 140 | 7.0686 | 9.4248 | 0.75 | 3.5024 | 0 | 0.4 | 0.076193 | 0.076193 | 3.9016
1320 | 36 | Pipe | 16 | 24.7574 | 140 | 7.0686 | 9.4248 | 0.75 | 3.5024 | 1.2053 |  | 0 | 1.2053 | 5.1069
| 36 | 45 Deg Bend | 16 | 24.7574 | 140 | 7.0686 | 9.4248 | 0.75 | 3.5024 | 0 | 0.4 | 0.076193 | 0.076193 | 5.1831
1320 | 36 | Pipe | 16 | 24.7574 | 140 | 7.0686 | 9.4248 | 0.75 | 3.5024 | 1.2053 |  | 0 | 1.2053 | 6.3884
| 36 | 45 Deg Bend | 16 | 24.7574 | 140 | 7.0686 | 9.4248 | 0.75 | 3.5024 | 0 | 0.4 | 0.076193 | 0.076193 | 6.4646
1320 | 36 | Pipe | 16 | 24.7574 | 140 | 7.0686 | 9.4248 | 0.75 | 3.5024 | 1.2053 |  | 0 | 1.2053 | 7.6699
| 36 | 90 Deg Bend | 16 | 24.7574 | 140 | 7.0686 | 9.4248 | 0.75 | 3.5024 | 0 | 0.2 | 0.038097 | 0.038097 | 7.708
1320 | 36 | Pipe | 16 | 24.7574 | 140 | 7.0686 | 9.4248 | 0.75 | 3.5024 | 1.2053 |  | 0 | 1.2053 | 8.9133
| 36 | Exit to Headworks | 16 | 24.7574 | 140 | 7.0686 | 9.4248 | 0.75 | 3.5024 | 0 | 1 | 0.19048 | 0.19048 | 9.1038
[13 empty] | Total | 9.1038
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 16 | 24.7574 | 100 | 7.0686 | 9.4248 | 0.75 | 3.5024 | 0 | 0.25 | 0.047621 | 0.047621 | 0.047621
| 36 | 30" X 36" Increaser | 16 | 24.7574 | 100 | 7.0686 | 9.4248 | 0.75 | 3.5024 | 0 | 0.25 | 0.047621 | 0.047621 | 0.095242
1320 | 36 | Pipe | 16 | 24.7574 | 100 | 7.0686 | 9.4248 | 0.75 | 3.5024 | 2.2461 |  | 0 | 2.2461 | 2.3414
| 36 | 90 Deg Bend | 16 | 24.7574 | 100 | 7.0686 | 9.4248 | 0.75 | 3.5024 | 0 | 0.2 | 0.038097 | 0.038097 | 2.3795
1320 | 36 | Pipe | 16 | 24.7574 | 100 | 7.0686 | 9.4248 | 0.75 | 3.5024 | 2.2461 |  | 0 | 2.2461 | 4.6256
| 36 | 45 Deg Bend | 16 | 24.7574 | 100 | 7.0686 | 9.4248 | 0.75 | 3.5024 | 0 | 0.4 | 0.076193 | 0.076193 | 4.7018
1320 | 36 | Pipe | 16 | 24.7574 | 100 | 7.0686 | 9.4248 | 0.75 | 3.5024 | 2.2461 |  | 0 | 2.2461 | 6.9479
| 36 | 45 Deg Bend | 16 | 24.7574 | 100 | 7.0686 | 9.4248 | 0.75 | 3.5024 | 0 | 0.4 | 0.076193 | 0.076193 | 7.0241
1320 | 36 | Pipe | 16 | 24.7574 | 100 | 7.0686 | 9.4248 | 0.75 | 3.5024 | 2.2461 |  | 0 | 2.2461 | 9.2702
| 36 | 45 Deg Bend | 16 | 24.7574 | 100 | 7.0686 | 9.4248 | 0.75 | 3.5024 | 0 | 0.4 | 0.076193 | 0.076193 | 9.3464
1320 | 36 | Pipe | 16 | 24.7574 | 100 | 7.0686 | 9.4248 | 0.75 | 3.5024 | 2.2461 |  | 0 | 2.2461 | 11.5925
| 36 | 45 Deg Bend | 16 | 24.7574 | 100 | 7.0686 | 9.4248 | 0.75 | 3.5024 | 0 | 0.4 | 0.076193 | 0.076193 | 11.6687
1320 | 36 | Pipe | 16 | 24.7574 | 100 | 7.0686 | 9.4248 | 0.75 | 3.5024 | 2.2461 |  | 0 | 2.2461 | 13.9148
| 36 | 90 Deg Bend | 16 | 24.7574 | 100 | 7.0686 | 9.4248 | 0.75 | 3.5024 | 0 | 0.2 | 0.038097 | 0.038097 | 13.9529
1320 | 36 | Pipe | 16 | 24.7574 | 100 | 7.0686 | 9.4248 | 0.75 | 3.5024 | 2.2461 |  | 0 | 2.2461 | 16.1991
| 36 | Exit to Headworks | 16 | 24.7574 | 100 | 7.0686 | 9.4248 | 0.75 | 3.5024 | 0 | 1 | 0.19048 | 0.19048 | 16.3895
[13 empty] | Total | 16.3895

## HL 17.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 17 | 26.3047 | 140 | 7.0686 | 9.4248 | 0.75 | 3.7213 | 0 | 0.25 | 0.053759 | 0.053759 | 0.053759
| 36 | 30" X 36" Increaser | 17 | 26.3047 | 140 | 7.0686 | 9.4248 | 0.75 | 3.7213 | 0 | 0.25 | 0.053759 | 0.053759 | 0.10752
1320 | 36 | Pipe | 17 | 26.3047 | 140 | 7.0686 | 9.4248 | 0.75 | 3.7213 | 1.3484 |  | 0 | 1.3484 | 1.4559
| 36 | 90 Deg Bend | 17 | 26.3047 | 140 | 7.0686 | 9.4248 | 0.75 | 3.7213 | 0 | 0.2 | 0.043008 | 0.043008 | 1.4989
1320 | 36 | Pipe | 17 | 26.3047 | 140 | 7.0686 | 9.4248 | 0.75 | 3.7213 | 1.3484 |  | 0 | 1.3484 | 2.8472
| 36 | 45 Deg Bend | 17 | 26.3047 | 140 | 7.0686 | 9.4248 | 0.75 | 3.7213 | 0 | 0.4 | 0.086015 | 0.086015 | 2.9333
1320 | 36 | Pipe | 17 | 26.3047 | 140 | 7.0686 | 9.4248 | 0.75 | 3.7213 | 1.3484 |  | 0 | 1.3484 | 4.2816
| 36 | 45 Deg Bend | 17 | 26.3047 | 140 | 7.0686 | 9.4248 | 0.75 | 3.7213 | 0 | 0.4 | 0.086015 | 0.086015 | 4.3676
1320 | 36 | Pipe | 17 | 26.3047 | 140 | 7.0686 | 9.4248 | 0.75 | 3.7213 | 1.3484 |  | 0 | 1.3484 | 5.716
| 36 | 45 Deg Bend | 17 | 26.3047 | 140 | 7.0686 | 9.4248 | 0.75 | 3.7213 | 0 | 0.4 | 0.086015 | 0.086015 | 5.802
1320 | 36 | Pipe | 17 | 26.3047 | 140 | 7.0686 | 9.4248 | 0.75 | 3.7213 | 1.3484 |  | 0 | 1.3484 | 7.1504
| 36 | 45 Deg Bend | 17 | 26.3047 | 140 | 7.0686 | 9.4248 | 0.75 | 3.7213 | 0 | 0.4 | 0.086015 | 0.086015 | 7.2364
1320 | 36 | Pipe | 17 | 26.3047 | 140 | 7.0686 | 9.4248 | 0.75 | 3.7213 | 1.3484 |  | 0 | 1.3484 | 8.5847
| 36 | 90 Deg Bend | 17 | 26.3047 | 140 | 7.0686 | 9.4248 | 0.75 | 3.7213 | 0 | 0.2 | 0.043008 | 0.043008 | 8.6277
1320 | 36 | Pipe | 17 | 26.3047 | 140 | 7.0686 | 9.4248 | 0.75 | 3.7213 | 1.3484 |  | 0 | 1.3484 | 9.9761
| 36 | Exit to Headworks | 17 | 26.3047 | 140 | 7.0686 | 9.4248 | 0.75 | 3.7213 | 0 | 1 | 0.21504 | 0.21504 | 10.1911
[13 empty] | Total | 10.1911
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 17 | 26.3047 | 100 | 7.0686 | 9.4248 | 0.75 | 3.7213 | 0 | 0.25 | 0.053759 | 0.053759 | 0.053759
| 36 | 30" X 36" Increaser | 17 | 26.3047 | 100 | 7.0686 | 9.4248 | 0.75 | 3.7213 | 0 | 0.25 | 0.053759 | 0.053759 | 0.10752
1320 | 36 | Pipe | 17 | 26.3047 | 100 | 7.0686 | 9.4248 | 0.75 | 3.7213 | 2.5127 |  | 0 | 2.5127 | 2.6202
| 36 | 90 Deg Bend | 17 | 26.3047 | 100 | 7.0686 | 9.4248 | 0.75 | 3.7213 | 0 | 0.2 | 0.043008 | 0.043008 | 2.6632
1320 | 36 | Pipe | 17 | 26.3047 | 100 | 7.0686 | 9.4248 | 0.75 | 3.7213 | 2.5127 |  | 0 | 2.5127 | 5.1759
| 36 | 45 Deg Bend | 17 | 26.3047 | 100 | 7.0686 | 9.4248 | 0.75 | 3.7213 | 0 | 0.4 | 0.086015 | 0.086015 | 5.262
1320 | 36 | Pipe | 17 | 26.3047 | 100 | 7.0686 | 9.4248 | 0.75 | 3.7213 | 2.5127 |  | 0 | 2.5127 | 7.7747
| 36 | 45 Deg Bend | 17 | 26.3047 | 100 | 7.0686 | 9.4248 | 0.75 | 3.7213 | 0 | 0.4 | 0.086015 | 0.086015 | 7.8607
1320 | 36 | Pipe | 17 | 26.3047 | 100 | 7.0686 | 9.4248 | 0.75 | 3.7213 | 2.5127 |  | 0 | 2.5127 | 10.3734
| 36 | 45 Deg Bend | 17 | 26.3047 | 100 | 7.0686 | 9.4248 | 0.75 | 3.7213 | 0 | 0.4 | 0.086015 | 0.086015 | 10.4594
1320 | 36 | Pipe | 17 | 26.3047 | 100 | 7.0686 | 9.4248 | 0.75 | 3.7213 | 2.5127 |  | 0 | 2.5127 | 12.9721
| 36 | 45 Deg Bend | 17 | 26.3047 | 100 | 7.0686 | 9.4248 | 0.75 | 3.7213 | 0 | 0.4 | 0.086015 | 0.086015 | 13.0581
1320 | 36 | Pipe | 17 | 26.3047 | 100 | 7.0686 | 9.4248 | 0.75 | 3.7213 | 2.5127 |  | 0 | 2.5127 | 15.5708
| 36 | 90 Deg Bend | 17 | 26.3047 | 100 | 7.0686 | 9.4248 | 0.75 | 3.7213 | 0 | 0.2 | 0.043008 | 0.043008 | 15.6138
1320 | 36 | Pipe | 17 | 26.3047 | 100 | 7.0686 | 9.4248 | 0.75 | 3.7213 | 2.5127 |  | 0 | 2.5127 | 18.1265
| 36 | Exit to Headworks | 17 | 26.3047 | 100 | 7.0686 | 9.4248 | 0.75 | 3.7213 | 0 | 1 | 0.21504 | 0.21504 | 18.3416
[13 empty] | Total | 18.3416

## HL 18.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 18 | 27.852 | 140 | 7.0686 | 9.4248 | 0.75 | 3.9402 | 0 | 0.25 | 0.06027 | 0.06027 | 0.06027
| 36 | 30" X 36" Increaser | 18 | 27.852 | 140 | 7.0686 | 9.4248 | 0.75 | 3.9402 | 0 | 0.25 | 0.06027 | 0.06027 | 0.12054
1320 | 36 | Pipe | 18 | 27.852 | 140 | 7.0686 | 9.4248 | 0.75 | 3.9402 | 1.4987 |  | 0 | 1.4987 | 1.6193
| 36 | 90 Deg Bend | 18 | 27.852 | 140 | 7.0686 | 9.4248 | 0.75 | 3.9402 | 0 | 0.2 | 0.048216 | 0.048216 | 1.6675
1320 | 36 | Pipe | 18 | 27.852 | 140 | 7.0686 | 9.4248 | 0.75 | 3.9402 | 1.4987 |  | 0 | 1.4987 | 3.1663
| 36 | 45 Deg Bend | 18 | 27.852 | 140 | 7.0686 | 9.4248 | 0.75 | 3.9402 | 0 | 0.4 | 0.096432 | 0.096432 | 3.2627
1320 | 36 | Pipe | 18 | 27.852 | 140 | 7.0686 | 9.4248 | 0.75 | 3.9402 | 1.4987 |  | 0 | 1.4987 | 4.7614
| 36 | 45 Deg Bend | 18 | 27.852 | 140 | 7.0686 | 9.4248 | 0.75 | 3.9402 | 0 | 0.4 | 0.096432 | 0.096432 | 4.8579
1320 | 36 | Pipe | 18 | 27.852 | 140 | 7.0686 | 9.4248 | 0.75 | 3.9402 | 1.4987 |  | 0 | 1.4987 | 6.3566
| 36 | 45 Deg Bend | 18 | 27.852 | 140 | 7.0686 | 9.4248 | 0.75 | 3.9402 | 0 | 0.4 | 0.096432 | 0.096432 | 6.453
1320 | 36 | Pipe | 18 | 27.852 | 140 | 7.0686 | 9.4248 | 0.75 | 3.9402 | 1.4987 |  | 0 | 1.4987 | 7.9518
| 36 | 45 Deg Bend | 18 | 27.852 | 140 | 7.0686 | 9.4248 | 0.75 | 3.9402 | 0 | 0.4 | 0.096432 | 0.096432 | 8.0482
1320 | 36 | Pipe | 18 | 27.852 | 140 | 7.0686 | 9.4248 | 0.75 | 3.9402 | 1.4987 |  | 0 | 1.4987 | 9.547
| 36 | 90 Deg Bend | 18 | 27.852 | 140 | 7.0686 | 9.4248 | 0.75 | 3.9402 | 0 | 0.2 | 0.048216 | 0.048216 | 9.5952
1320 | 36 | Pipe | 18 | 27.852 | 140 | 7.0686 | 9.4248 | 0.75 | 3.9402 | 1.4987 |  | 0 | 1.4987 | 11.0939
| 36 | Exit to Headworks | 18 | 27.852 | 140 | 7.0686 | 9.4248 | 0.75 | 3.9402 | 0 | 1 | 0.24108 | 0.24108 | 11.335
[13 empty] | Total | 11.335
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 18 | 27.852 | 100 | 7.0686 | 9.4248 | 0.75 | 3.9402 | 0 | 0.25 | 0.06027 | 0.06027 | 0.06027
| 36 | 30" X 36" Increaser | 18 | 27.852 | 100 | 7.0686 | 9.4248 | 0.75 | 3.9402 | 0 | 0.25 | 0.06027 | 0.06027 | 0.12054
1320 | 36 | Pipe | 18 | 27.852 | 100 | 7.0686 | 9.4248 | 0.75 | 3.9402 | 2.793 |  | 0 | 2.793 | 2.9135
| 36 | 90 Deg Bend | 18 | 27.852 | 100 | 7.0686 | 9.4248 | 0.75 | 3.9402 | 0 | 0.2 | 0.048216 | 0.048216 | 2.9617
1320 | 36 | Pipe | 18 | 27.852 | 100 | 7.0686 | 9.4248 | 0.75 | 3.9402 | 2.793 |  | 0 | 2.793 | 5.7547
| 36 | 45 Deg Bend | 18 | 27.852 | 100 | 7.0686 | 9.4248 | 0.75 | 3.9402 | 0 | 0.4 | 0.096432 | 0.096432 | 5.8511
1320 | 36 | Pipe | 18 | 27.852 | 100 | 7.0686 | 9.4248 | 0.75 | 3.9402 | 2.793 |  | 0 | 2.793 | 8.6441
| 36 | 45 Deg Bend | 18 | 27.852 | 100 | 7.0686 | 9.4248 | 0.75 | 3.9402 | 0 | 0.4 | 0.096432 | 0.096432 | 8.7405
1320 | 36 | Pipe | 18 | 27.852 | 100 | 7.0686 | 9.4248 | 0.75 | 3.9402 | 2.793 |  | 0 | 2.793 | 11.5335
| 36 | 45 Deg Bend | 18 | 27.852 | 100 | 7.0686 | 9.4248 | 0.75 | 3.9402 | 0 | 0.4 | 0.096432 | 0.096432 | 11.6299
1320 | 36 | Pipe | 18 | 27.852 | 100 | 7.0686 | 9.4248 | 0.75 | 3.9402 | 2.793 |  | 0 | 2.793 | 14.4229
| 36 | 45 Deg Bend | 18 | 27.852 | 100 | 7.0686 | 9.4248 | 0.75 | 3.9402 | 0 | 0.4 | 0.096432 | 0.096432 | 14.5193
1320 | 36 | Pipe | 18 | 27.852 | 100 | 7.0686 | 9.4248 | 0.75 | 3.9402 | 2.793 |  | 0 | 2.793 | 17.3123
| 36 | 90 Deg Bend | 18 | 27.852 | 100 | 7.0686 | 9.4248 | 0.75 | 3.9402 | 0 | 0.2 | 0.048216 | 0.048216 | 17.3605
1320 | 36 | Pipe | 18 | 27.852 | 100 | 7.0686 | 9.4248 | 0.75 | 3.9402 | 2.793 |  | 0 | 2.793 | 20.1535
| 36 | Exit to Headworks | 18 | 27.852 | 100 | 7.0686 | 9.4248 | 0.75 | 3.9402 | 0 | 1 | 0.24108 | 0.24108 | 20.3945
[13 empty] | Total | 20.3945

## HL 19.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 19 | 29.3994 | 140 | 7.0686 | 9.4248 | 0.75 | 4.1592 | 0 | 0.25 | 0.067153 | 0.067153 | 0.067153
| 36 | 30" X 36" Increaser | 19 | 29.3994 | 140 | 7.0686 | 9.4248 | 0.75 | 4.1592 | 0 | 0.25 | 0.067153 | 0.067153 | 0.13431
1320 | 36 | Pipe | 19 | 29.3994 | 140 | 7.0686 | 9.4248 | 0.75 | 4.1592 | 1.6564 |  | 0 | 1.6564 | 1.7907
| 36 | 90 Deg Bend | 19 | 29.3994 | 140 | 7.0686 | 9.4248 | 0.75 | 4.1592 | 0 | 0.2 | 0.053722 | 0.053722 | 1.8444
1320 | 36 | Pipe | 19 | 29.3994 | 140 | 7.0686 | 9.4248 | 0.75 | 4.1592 | 1.6564 |  | 0 | 1.6564 | 3.5009
| 36 | 45 Deg Bend | 19 | 29.3994 | 140 | 7.0686 | 9.4248 | 0.75 | 4.1592 | 0 | 0.4 | 0.10744 | 0.10744 | 3.6083
1320 | 36 | Pipe | 19 | 29.3994 | 140 | 7.0686 | 9.4248 | 0.75 | 4.1592 | 1.6564 |  | 0 | 1.6564 | 5.2647
| 36 | 45 Deg Bend | 19 | 29.3994 | 140 | 7.0686 | 9.4248 | 0.75 | 4.1592 | 0 | 0.4 | 0.10744 | 0.10744 | 5.3722
1320 | 36 | Pipe | 19 | 29.3994 | 140 | 7.0686 | 9.4248 | 0.75 | 4.1592 | 1.6564 |  | 0 | 1.6564 | 7.0286
| 36 | 45 Deg Bend | 19 | 29.3994 | 140 | 7.0686 | 9.4248 | 0.75 | 4.1592 | 0 | 0.4 | 0.10744 | 0.10744 | 7.136
1320 | 36 | Pipe | 19 | 29.3994 | 140 | 7.0686 | 9.4248 | 0.75 | 4.1592 | 1.6564 |  | 0 | 1.6564 | 8.7924
| 36 | 45 Deg Bend | 19 | 29.3994 | 140 | 7.0686 | 9.4248 | 0.75 | 4.1592 | 0 | 0.4 | 0.10744 | 0.10744 | 8.8999
1320 | 36 | Pipe | 19 | 29.3994 | 140 | 7.0686 | 9.4248 | 0.75 | 4.1592 | 1.6564 |  | 0 | 1.6564 | 10.5563
| 36 | 90 Deg Bend | 19 | 29.3994 | 140 | 7.0686 | 9.4248 | 0.75 | 4.1592 | 0 | 0.2 | 0.053722 | 0.053722 | 10.61
1320 | 36 | Pipe | 19 | 29.3994 | 140 | 7.0686 | 9.4248 | 0.75 | 4.1592 | 1.6564 |  | 0 | 1.6564 | 12.2664
| 36 | Exit to Headworks | 19 | 29.3994 | 140 | 7.0686 | 9.4248 | 0.75 | 4.1592 | 0 | 1 | 0.26861 | 0.26861 | 12.535
[13 empty] | Total | 12.535
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 19 | 29.3994 | 100 | 7.0686 | 9.4248 | 0.75 | 4.1592 | 0 | 0.25 | 0.067153 | 0.067153 | 0.067153
| 36 | 30" X 36" Increaser | 19 | 29.3994 | 100 | 7.0686 | 9.4248 | 0.75 | 4.1592 | 0 | 0.25 | 0.067153 | 0.067153 | 0.13431
1320 | 36 | Pipe | 19 | 29.3994 | 100 | 7.0686 | 9.4248 | 0.75 | 4.1592 | 3.0868 |  | 0 | 3.0868 | 3.2211
| 36 | 90 Deg Bend | 19 | 29.3994 | 100 | 7.0686 | 9.4248 | 0.75 | 4.1592 | 0 | 0.2 | 0.053722 | 0.053722 | 3.2748
1320 | 36 | Pipe | 19 | 29.3994 | 100 | 7.0686 | 9.4248 | 0.75 | 4.1592 | 3.0868 |  | 0 | 3.0868 | 6.3616
| 36 | 45 Deg Bend | 19 | 29.3994 | 100 | 7.0686 | 9.4248 | 0.75 | 4.1592 | 0 | 0.4 | 0.10744 | 0.10744 | 6.469
1320 | 36 | Pipe | 19 | 29.3994 | 100 | 7.0686 | 9.4248 | 0.75 | 4.1592 | 3.0868 |  | 0 | 3.0868 | 9.5558
| 36 | 45 Deg Bend | 19 | 29.3994 | 100 | 7.0686 | 9.4248 | 0.75 | 4.1592 | 0 | 0.4 | 0.10744 | 0.10744 | 9.6633
1320 | 36 | Pipe | 19 | 29.3994 | 100 | 7.0686 | 9.4248 | 0.75 | 4.1592 | 3.0868 |  | 0 | 3.0868 | 12.75
| 36 | 45 Deg Bend | 19 | 29.3994 | 100 | 7.0686 | 9.4248 | 0.75 | 4.1592 | 0 | 0.4 | 0.10744 | 0.10744 | 12.8575
1320 | 36 | Pipe | 19 | 29.3994 | 100 | 7.0686 | 9.4248 | 0.75 | 4.1592 | 3.0868 |  | 0 | 3.0868 | 15.9443
| 36 | 45 Deg Bend | 19 | 29.3994 | 100 | 7.0686 | 9.4248 | 0.75 | 4.1592 | 0 | 0.4 | 0.10744 | 0.10744 | 16.0517
1320 | 36 | Pipe | 19 | 29.3994 | 100 | 7.0686 | 9.4248 | 0.75 | 4.1592 | 3.0868 |  | 0 | 3.0868 | 19.1385
| 36 | 90 Deg Bend | 19 | 29.3994 | 100 | 7.0686 | 9.4248 | 0.75 | 4.1592 | 0 | 0.2 | 0.053722 | 0.053722 | 19.1922
1320 | 36 | Pipe | 19 | 29.3994 | 100 | 7.0686 | 9.4248 | 0.75 | 4.1592 | 3.0868 |  | 0 | 3.0868 | 22.279
| 36 | Exit to Headworks | 19 | 29.3994 | 100 | 7.0686 | 9.4248 | 0.75 | 4.1592 | 0 | 1 | 0.26861 | 0.26861 | 22.5476
[13 empty] | Total | 22.5476

## HL 20.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 20 | 30.9467 | 140 | 7.0686 | 9.4248 | 0.75 | 4.3781 | 0 | 0.25 | 0.074407 | 0.074407 | 0.074407
| 36 | 30" X 36" Increaser | 20 | 30.9467 | 140 | 7.0686 | 9.4248 | 0.75 | 4.3781 | 0 | 0.25 | 0.074407 | 0.074407 | 0.14881
1320 | 36 | Pipe | 20 | 30.9467 | 140 | 7.0686 | 9.4248 | 0.75 | 4.3781 | 1.8213 |  | 0 | 1.8213 | 1.9701
| 36 | 90 Deg Bend | 20 | 30.9467 | 140 | 7.0686 | 9.4248 | 0.75 | 4.3781 | 0 | 0.2 | 0.059526 | 0.059526 | 2.0296
1320 | 36 | Pipe | 20 | 30.9467 | 140 | 7.0686 | 9.4248 | 0.75 | 4.3781 | 1.8213 |  | 0 | 1.8213 | 3.8509
| 36 | 45 Deg Bend | 20 | 30.9467 | 140 | 7.0686 | 9.4248 | 0.75 | 4.3781 | 0 | 0.4 | 0.11905 | 0.11905 | 3.97
1320 | 36 | Pipe | 20 | 30.9467 | 140 | 7.0686 | 9.4248 | 0.75 | 4.3781 | 1.8213 |  | 0 | 1.8213 | 5.7913
| 36 | 45 Deg Bend | 20 | 30.9467 | 140 | 7.0686 | 9.4248 | 0.75 | 4.3781 | 0 | 0.4 | 0.11905 | 0.11905 | 5.9103
1320 | 36 | Pipe | 20 | 30.9467 | 140 | 7.0686 | 9.4248 | 0.75 | 4.3781 | 1.8213 |  | 0 | 1.8213 | 7.7316
| 36 | 45 Deg Bend | 20 | 30.9467 | 140 | 7.0686 | 9.4248 | 0.75 | 4.3781 | 0 | 0.4 | 0.11905 | 0.11905 | 7.8507
1320 | 36 | Pipe | 20 | 30.9467 | 140 | 7.0686 | 9.4248 | 0.75 | 4.3781 | 1.8213 |  | 0 | 1.8213 | 9.672
| 36 | 45 Deg Bend | 20 | 30.9467 | 140 | 7.0686 | 9.4248 | 0.75 | 4.3781 | 0 | 0.4 | 0.11905 | 0.11905 | 9.791
1320 | 36 | Pipe | 20 | 30.9467 | 140 | 7.0686 | 9.4248 | 0.75 | 4.3781 | 1.8213 |  | 0 | 1.8213 | 11.6123
| 36 | 90 Deg Bend | 20 | 30.9467 | 140 | 7.0686 | 9.4248 | 0.75 | 4.3781 | 0 | 0.2 | 0.059526 | 0.059526 | 11.6718
1320 | 36 | Pipe | 20 | 30.9467 | 140 | 7.0686 | 9.4248 | 0.75 | 4.3781 | 1.8213 |  | 0 | 1.8213 | 13.4931
| 36 | Exit to Headworks | 20 | 30.9467 | 140 | 7.0686 | 9.4248 | 0.75 | 4.3781 | 0 | 1 | 0.29763 | 0.29763 | 13.7908
[13 empty] | Total | 13.7908
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 20 | 30.9467 | 100 | 7.0686 | 9.4248 | 0.75 | 4.3781 | 0 | 0.25 | 0.074407 | 0.074407 | 0.074407
| 36 | 30" X 36" Increaser | 20 | 30.9467 | 100 | 7.0686 | 9.4248 | 0.75 | 4.3781 | 0 | 0.25 | 0.074407 | 0.074407 | 0.14881
1320 | 36 | Pipe | 20 | 30.9467 | 100 | 7.0686 | 9.4248 | 0.75 | 4.3781 | 3.394 |  | 0 | 3.394 | 3.5429
| 36 | 90 Deg Bend | 20 | 30.9467 | 100 | 7.0686 | 9.4248 | 0.75 | 4.3781 | 0 | 0.2 | 0.059526 | 0.059526 | 3.6024
1320 | 36 | Pipe | 20 | 30.9467 | 100 | 7.0686 | 9.4248 | 0.75 | 4.3781 | 3.394 |  | 0 | 3.394 | 6.9964
| 36 | 45 Deg Bend | 20 | 30.9467 | 100 | 7.0686 | 9.4248 | 0.75 | 4.3781 | 0 | 0.4 | 0.11905 | 0.11905 | 7.1155
1320 | 36 | Pipe | 20 | 30.9467 | 100 | 7.0686 | 9.4248 | 0.75 | 4.3781 | 3.394 |  | 0 | 3.394 | 10.5095
| 36 | 45 Deg Bend | 20 | 30.9467 | 100 | 7.0686 | 9.4248 | 0.75 | 4.3781 | 0 | 0.4 | 0.11905 | 0.11905 | 10.6286
1320 | 36 | Pipe | 20 | 30.9467 | 100 | 7.0686 | 9.4248 | 0.75 | 4.3781 | 3.394 |  | 0 | 3.394 | 14.0226
| 36 | 45 Deg Bend | 20 | 30.9467 | 100 | 7.0686 | 9.4248 | 0.75 | 4.3781 | 0 | 0.4 | 0.11905 | 0.11905 | 14.1417
1320 | 36 | Pipe | 20 | 30.9467 | 100 | 7.0686 | 9.4248 | 0.75 | 4.3781 | 3.394 |  | 0 | 3.394 | 17.5357
| 36 | 45 Deg Bend | 20 | 30.9467 | 100 | 7.0686 | 9.4248 | 0.75 | 4.3781 | 0 | 0.4 | 0.11905 | 0.11905 | 17.6547
1320 | 36 | Pipe | 20 | 30.9467 | 100 | 7.0686 | 9.4248 | 0.75 | 4.3781 | 3.394 |  | 0 | 3.394 | 21.0488
| 36 | 90 Deg Bend | 20 | 30.9467 | 100 | 7.0686 | 9.4248 | 0.75 | 4.3781 | 0 | 0.2 | 0.059526 | 0.059526 | 21.1083
1320 | 36 | Pipe | 20 | 30.9467 | 100 | 7.0686 | 9.4248 | 0.75 | 4.3781 | 3.394 |  | 0 | 3.394 | 24.5023
| 36 | Exit to Headworks | 20 | 30.9467 | 100 | 7.0686 | 9.4248 | 0.75 | 4.3781 | 0 | 1 | 0.29763 | 0.29763 | 24.8
[13 empty] | Total | 24.8

## HL 21.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 21 | 32.4941 | 140 | 7.0686 | 9.4248 | 0.75 | 4.597 | 0 | 0.25 | 0.082034 | 0.082034 | 0.082034
| 36 | 30" X 36" Increaser | 21 | 32.4941 | 140 | 7.0686 | 9.4248 | 0.75 | 4.597 | 0 | 0.25 | 0.082034 | 0.082034 | 0.16407
1320 | 36 | Pipe | 21 | 32.4941 | 140 | 7.0686 | 9.4248 | 0.75 | 4.597 | 1.9933 |  | 0 | 1.9933 | 2.1574
| 36 | 90 Deg Bend | 21 | 32.4941 | 140 | 7.0686 | 9.4248 | 0.75 | 4.597 | 0 | 0.2 | 0.065627 | 0.065627 | 2.223
1320 | 36 | Pipe | 21 | 32.4941 | 140 | 7.0686 | 9.4248 | 0.75 | 4.597 | 1.9933 |  | 0 | 1.9933 | 4.2164
| 36 | 45 Deg Bend | 21 | 32.4941 | 140 | 7.0686 | 9.4248 | 0.75 | 4.597 | 0 | 0.4 | 0.13125 | 0.13125 | 4.3476
1320 | 36 | Pipe | 21 | 32.4941 | 140 | 7.0686 | 9.4248 | 0.75 | 4.597 | 1.9933 |  | 0 | 1.9933 | 6.341
| 36 | 45 Deg Bend | 21 | 32.4941 | 140 | 7.0686 | 9.4248 | 0.75 | 4.597 | 0 | 0.4 | 0.13125 | 0.13125 | 6.4722
1320 | 36 | Pipe | 21 | 32.4941 | 140 | 7.0686 | 9.4248 | 0.75 | 4.597 | 1.9933 |  | 0 | 1.9933 | 8.4655
| 36 | 45 Deg Bend | 21 | 32.4941 | 140 | 7.0686 | 9.4248 | 0.75 | 4.597 | 0 | 0.4 | 0.13125 | 0.13125 | 8.5968
1320 | 36 | Pipe | 21 | 32.4941 | 140 | 7.0686 | 9.4248 | 0.75 | 4.597 | 1.9933 |  | 0 | 1.9933 | 10.5901
| 36 | 45 Deg Bend | 21 | 32.4941 | 140 | 7.0686 | 9.4248 | 0.75 | 4.597 | 0 | 0.4 | 0.13125 | 0.13125 | 10.7214
1320 | 36 | Pipe | 21 | 32.4941 | 140 | 7.0686 | 9.4248 | 0.75 | 4.597 | 1.9933 |  | 0 | 1.9933 | 12.7147
| 36 | 90 Deg Bend | 21 | 32.4941 | 140 | 7.0686 | 9.4248 | 0.75 | 4.597 | 0 | 0.2 | 0.065627 | 0.065627 | 12.7803
1320 | 36 | Pipe | 21 | 32.4941 | 140 | 7.0686 | 9.4248 | 0.75 | 4.597 | 1.9933 |  | 0 | 1.9933 | 14.7737
| 36 | Exit to Headworks | 21 | 32.4941 | 140 | 7.0686 | 9.4248 | 0.75 | 4.597 | 0 | 1 | 0.32814 | 0.32814 | 15.1018
[13 empty] | Total | 15.1018
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 21 | 32.4941 | 100 | 7.0686 | 9.4248 | 0.75 | 4.597 | 0 | 0.25 | 0.082034 | 0.082034 | 0.082034
| 36 | 30" X 36" Increaser | 21 | 32.4941 | 100 | 7.0686 | 9.4248 | 0.75 | 4.597 | 0 | 0.25 | 0.082034 | 0.082034 | 0.16407
1320 | 36 | Pipe | 21 | 32.4941 | 100 | 7.0686 | 9.4248 | 0.75 | 4.597 | 3.7146 |  | 0 | 3.7146 | 3.8787
| 36 | 90 Deg Bend | 21 | 32.4941 | 100 | 7.0686 | 9.4248 | 0.75 | 4.597 | 0 | 0.2 | 0.065627 | 0.065627 | 3.9443
1320 | 36 | Pipe | 21 | 32.4941 | 100 | 7.0686 | 9.4248 | 0.75 | 4.597 | 3.7146 |  | 0 | 3.7146 | 7.659
| 36 | 45 Deg Bend | 21 | 32.4941 | 100 | 7.0686 | 9.4248 | 0.75 | 4.597 | 0 | 0.4 | 0.13125 | 0.13125 | 7.7902
1320 | 36 | Pipe | 21 | 32.4941 | 100 | 7.0686 | 9.4248 | 0.75 | 4.597 | 3.7146 |  | 0 | 3.7146 | 11.5049
| 36 | 45 Deg Bend | 21 | 32.4941 | 100 | 7.0686 | 9.4248 | 0.75 | 4.597 | 0 | 0.4 | 0.13125 | 0.13125 | 11.6361
1320 | 36 | Pipe | 21 | 32.4941 | 100 | 7.0686 | 9.4248 | 0.75 | 4.597 | 3.7146 |  | 0 | 3.7146 | 15.3508
| 36 | 45 Deg Bend | 21 | 32.4941 | 100 | 7.0686 | 9.4248 | 0.75 | 4.597 | 0 | 0.4 | 0.13125 | 0.13125 | 15.482
1320 | 36 | Pipe | 21 | 32.4941 | 100 | 7.0686 | 9.4248 | 0.75 | 4.597 | 3.7146 |  | 0 | 3.7146 | 19.1967
| 36 | 45 Deg Bend | 21 | 32.4941 | 100 | 7.0686 | 9.4248 | 0.75 | 4.597 | 0 | 0.4 | 0.13125 | 0.13125 | 19.3279
1320 | 36 | Pipe | 21 | 32.4941 | 100 | 7.0686 | 9.4248 | 0.75 | 4.597 | 3.7146 |  | 0 | 3.7146 | 23.0426
| 36 | 90 Deg Bend | 21 | 32.4941 | 100 | 7.0686 | 9.4248 | 0.75 | 4.597 | 0 | 0.2 | 0.065627 | 0.065627 | 23.1082
1320 | 36 | Pipe | 21 | 32.4941 | 100 | 7.0686 | 9.4248 | 0.75 | 4.597 | 3.7146 |  | 0 | 3.7146 | 26.8228
| 36 | Exit to Headworks | 21 | 32.4941 | 100 | 7.0686 | 9.4248 | 0.75 | 4.597 | 0 | 1 | 0.32814 | 0.32814 | 27.151
[13 empty] | Total | 27.151

## HL 22.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 22 | 34.0414 | 140 | 7.0686 | 9.4248 | 0.75 | 4.8159 | 0 | 0.25 | 0.090033 | 0.090033 | 0.090033
| 36 | 30" X 36" Increaser | 22 | 34.0414 | 140 | 7.0686 | 9.4248 | 0.75 | 4.8159 | 0 | 0.25 | 0.090033 | 0.090033 | 0.18007
1320 | 36 | Pipe | 22 | 34.0414 | 140 | 7.0686 | 9.4248 | 0.75 | 4.8159 | 2.1725 |  | 0 | 2.1725 | 2.3525
| 36 | 90 Deg Bend | 22 | 34.0414 | 140 | 7.0686 | 9.4248 | 0.75 | 4.8159 | 0 | 0.2 | 0.072026 | 0.072026 | 2.4246
1320 | 36 | Pipe | 22 | 34.0414 | 140 | 7.0686 | 9.4248 | 0.75 | 4.8159 | 2.1725 |  | 0 | 2.1725 | 4.5971
| 36 | 45 Deg Bend | 22 | 34.0414 | 140 | 7.0686 | 9.4248 | 0.75 | 4.8159 | 0 | 0.4 | 0.14405 | 0.14405 | 4.7411
1320 | 36 | Pipe | 22 | 34.0414 | 140 | 7.0686 | 9.4248 | 0.75 | 4.8159 | 2.1725 |  | 0 | 2.1725 | 6.9136
| 36 | 45 Deg Bend | 22 | 34.0414 | 140 | 7.0686 | 9.4248 | 0.75 | 4.8159 | 0 | 0.4 | 0.14405 | 0.14405 | 7.0576
1320 | 36 | Pipe | 22 | 34.0414 | 140 | 7.0686 | 9.4248 | 0.75 | 4.8159 | 2.1725 |  | 0 | 2.1725 | 9.2301
| 36 | 45 Deg Bend | 22 | 34.0414 | 140 | 7.0686 | 9.4248 | 0.75 | 4.8159 | 0 | 0.4 | 0.14405 | 0.14405 | 9.3742
1320 | 36 | Pipe | 22 | 34.0414 | 140 | 7.0686 | 9.4248 | 0.75 | 4.8159 | 2.1725 |  | 0 | 2.1725 | 11.5467
| 36 | 45 Deg Bend | 22 | 34.0414 | 140 | 7.0686 | 9.4248 | 0.75 | 4.8159 | 0 | 0.4 | 0.14405 | 0.14405 | 11.6907
1320 | 36 | Pipe | 22 | 34.0414 | 140 | 7.0686 | 9.4248 | 0.75 | 4.8159 | 2.1725 |  | 0 | 2.1725 | 13.8632
| 36 | 90 Deg Bend | 22 | 34.0414 | 140 | 7.0686 | 9.4248 | 0.75 | 4.8159 | 0 | 0.2 | 0.072026 | 0.072026 | 13.9352
1320 | 36 | Pipe | 22 | 34.0414 | 140 | 7.0686 | 9.4248 | 0.75 | 4.8159 | 2.1725 |  | 0 | 2.1725 | 16.1077
| 36 | Exit to Headworks | 22 | 34.0414 | 140 | 7.0686 | 9.4248 | 0.75 | 4.8159 | 0 | 1 | 0.36013 | 0.36013 | 16.4678
[13 empty] | Total | 16.4678
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 22 | 34.0414 | 100 | 7.0686 | 9.4248 | 0.75 | 4.8159 | 0 | 0.25 | 0.090033 | 0.090033 | 0.090033
| 36 | 30" X 36" Increaser | 22 | 34.0414 | 100 | 7.0686 | 9.4248 | 0.75 | 4.8159 | 0 | 0.25 | 0.090033 | 0.090033 | 0.18007
1320 | 36 | Pipe | 22 | 34.0414 | 100 | 7.0686 | 9.4248 | 0.75 | 4.8159 | 4.0485 |  | 0 | 4.0485 | 4.2286
| 36 | 90 Deg Bend | 22 | 34.0414 | 100 | 7.0686 | 9.4248 | 0.75 | 4.8159 | 0 | 0.2 | 0.072026 | 0.072026 | 4.3006
1320 | 36 | Pipe | 22 | 34.0414 | 100 | 7.0686 | 9.4248 | 0.75 | 4.8159 | 4.0485 |  | 0 | 4.0485 | 8.3491
| 36 | 45 Deg Bend | 22 | 34.0414 | 100 | 7.0686 | 9.4248 | 0.75 | 4.8159 | 0 | 0.4 | 0.14405 | 0.14405 | 8.4931
1320 | 36 | Pipe | 22 | 34.0414 | 100 | 7.0686 | 9.4248 | 0.75 | 4.8159 | 4.0485 |  | 0 | 4.0485 | 12.5416
| 36 | 45 Deg Bend | 22 | 34.0414 | 100 | 7.0686 | 9.4248 | 0.75 | 4.8159 | 0 | 0.4 | 0.14405 | 0.14405 | 12.6857
1320 | 36 | Pipe | 22 | 34.0414 | 100 | 7.0686 | 9.4248 | 0.75 | 4.8159 | 4.0485 |  | 0 | 4.0485 | 16.7342
| 36 | 45 Deg Bend | 22 | 34.0414 | 100 | 7.0686 | 9.4248 | 0.75 | 4.8159 | 0 | 0.4 | 0.14405 | 0.14405 | 16.8782
1320 | 36 | Pipe | 22 | 34.0414 | 100 | 7.0686 | 9.4248 | 0.75 | 4.8159 | 4.0485 |  | 0 | 4.0485 | 20.9267
| 36 | 45 Deg Bend | 22 | 34.0414 | 100 | 7.0686 | 9.4248 | 0.75 | 4.8159 | 0 | 0.4 | 0.14405 | 0.14405 | 21.0708
1320 | 36 | Pipe | 22 | 34.0414 | 100 | 7.0686 | 9.4248 | 0.75 | 4.8159 | 4.0485 |  | 0 | 4.0485 | 25.1193
| 36 | 90 Deg Bend | 22 | 34.0414 | 100 | 7.0686 | 9.4248 | 0.75 | 4.8159 | 0 | 0.2 | 0.072026 | 0.072026 | 25.1913
1320 | 36 | Pipe | 22 | 34.0414 | 100 | 7.0686 | 9.4248 | 0.75 | 4.8159 | 4.0485 |  | 0 | 4.0485 | 29.2398
| 36 | Exit to Headworks | 22 | 34.0414 | 100 | 7.0686 | 9.4248 | 0.75 | 4.8159 | 0 | 1 | 0.36013 | 0.36013 | 29.5999
[13 empty] | Total | 29.5999
.

## HL 23.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 23 | 35.5887 | 140 | 7.0686 | 9.4248 | 0.75 | 5.0348 | 0 | 0.25 | 0.098404 | 0.098404 | 0.098404
| 36 | 30" X 36" Increaser | 23 | 35.5887 | 140 | 7.0686 | 9.4248 | 0.75 | 5.0348 | 0 | 0.25 | 0.098404 | 0.098404 | 0.19681
1320 | 36 | Pipe | 23 | 35.5887 | 140 | 7.0686 | 9.4248 | 0.75 | 5.0348 | 2.3587 |  | 0 | 2.3587 | 2.5555
| 36 | 90 Deg Bend | 23 | 35.5887 | 140 | 7.0686 | 9.4248 | 0.75 | 5.0348 | 0 | 0.2 | 0.078723 | 0.078723 | 2.6342
1320 | 36 | Pipe | 23 | 35.5887 | 140 | 7.0686 | 9.4248 | 0.75 | 5.0348 | 2.3587 |  | 0 | 2.3587 | 4.9929
| 36 | 45 Deg Bend | 23 | 35.5887 | 140 | 7.0686 | 9.4248 | 0.75 | 5.0348 | 0 | 0.4 | 0.15745 | 0.15745 | 5.1504
1320 | 36 | Pipe | 23 | 35.5887 | 140 | 7.0686 | 9.4248 | 0.75 | 5.0348 | 2.3587 |  | 0 | 2.3587 | 7.509
| 36 | 45 Deg Bend | 23 | 35.5887 | 140 | 7.0686 | 9.4248 | 0.75 | 5.0348 | 0 | 0.4 | 0.15745 | 0.15745 | 7.6665
1320 | 36 | Pipe | 23 | 35.5887 | 140 | 7.0686 | 9.4248 | 0.75 | 5.0348 | 2.3587 |  | 0 | 2.3587 | 10.0252
| 36 | 45 Deg Bend | 23 | 35.5887 | 140 | 7.0686 | 9.4248 | 0.75 | 5.0348 | 0 | 0.4 | 0.15745 | 0.15745 | 10.1826
1320 | 36 | Pipe | 23 | 35.5887 | 140 | 7.0686 | 9.4248 | 0.75 | 5.0348 | 2.3587 |  | 0 | 2.3587 | 12.5413
| 36 | 45 Deg Bend | 23 | 35.5887 | 140 | 7.0686 | 9.4248 | 0.75 | 5.0348 | 0 | 0.4 | 0.15745 | 0.15745 | 12.6988
1320 | 36 | Pipe | 23 | 35.5887 | 140 | 7.0686 | 9.4248 | 0.75 | 5.0348 | 2.3587 |  | 0 | 2.3587 | 15.0575
| 36 | 90 Deg Bend | 23 | 35.5887 | 140 | 7.0686 | 9.4248 | 0.75 | 5.0348 | 0 | 0.2 | 0.078723 | 0.078723 | 15.1362
1320 | 36 | Pipe | 23 | 35.5887 | 140 | 7.0686 | 9.4248 | 0.75 | 5.0348 | 2.3587 |  | 0 | 2.3587 | 17.4949
| 36 | Exit to Headworks | 23 | 35.5887 | 140 | 7.0686 | 9.4248 | 0.75 | 5.0348 | 0 | 1 | 0.39362 | 0.39362 | 17.8885
[13 empty] | Total | 17.8885
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 23 | 35.5887 | 100 | 7.0686 | 9.4248 | 0.75 | 5.0348 | 0 | 0.25 | 0.098404 | 0.098404 | 0.098404
| 36 | 30" X 36" Increaser | 23 | 35.5887 | 100 | 7.0686 | 9.4248 | 0.75 | 5.0348 | 0 | 0.25 | 0.098404 | 0.098404 | 0.19681
1320 | 36 | Pipe | 23 | 35.5887 | 100 | 7.0686 | 9.4248 | 0.75 | 5.0348 | 4.3955 |  | 0 | 4.3955 | 4.5923
| 36 | 90 Deg Bend | 23 | 35.5887 | 100 | 7.0686 | 9.4248 | 0.75 | 5.0348 | 0 | 0.2 | 0.078723 | 0.078723 | 4.671
1320 | 36 | Pipe | 23 | 35.5887 | 100 | 7.0686 | 9.4248 | 0.75 | 5.0348 | 4.3955 |  | 0 | 4.3955 | 9.0665
| 36 | 45 Deg Bend | 23 | 35.5887 | 100 | 7.0686 | 9.4248 | 0.75 | 5.0348 | 0 | 0.4 | 0.15745 | 0.15745 | 9.224
1320 | 36 | Pipe | 23 | 35.5887 | 100 | 7.0686 | 9.4248 | 0.75 | 5.0348 | 4.3955 |  | 0 | 4.3955 | 13.6195
| 36 | 45 Deg Bend | 23 | 35.5887 | 100 | 7.0686 | 9.4248 | 0.75 | 5.0348 | 0 | 0.4 | 0.15745 | 0.15745 | 13.7769
1320 | 36 | Pipe | 23 | 35.5887 | 100 | 7.0686 | 9.4248 | 0.75 | 5.0348 | 4.3955 |  | 0 | 4.3955 | 18.1724
| 36 | 45 Deg Bend | 23 | 35.5887 | 100 | 7.0686 | 9.4248 | 0.75 | 5.0348 | 0 | 0.4 | 0.15745 | 0.15745 | 18.3299
1320 | 36 | Pipe | 23 | 35.5887 | 100 | 7.0686 | 9.4248 | 0.75 | 5.0348 | 4.3955 |  | 0 | 4.3955 | 22.7253
| 36 | 45 Deg Bend | 23 | 35.5887 | 100 | 7.0686 | 9.4248 | 0.75 | 5.0348 | 0 | 0.4 | 0.15745 | 0.15745 | 22.8828
1320 | 36 | Pipe | 23 | 35.5887 | 100 | 7.0686 | 9.4248 | 0.75 | 5.0348 | 4.3955 |  | 0 | 4.3955 | 27.2783
| 36 | 90 Deg Bend | 23 | 35.5887 | 100 | 7.0686 | 9.4248 | 0.75 | 5.0348 | 0 | 0.2 | 0.078723 | 0.078723 | 27.357
1320 | 36 | Pipe | 23 | 35.5887 | 100 | 7.0686 | 9.4248 | 0.75 | 5.0348 | 4.3955 |  | 0 | 4.3955 | 31.7525
| 36 | Exit to Headworks | 23 | 35.5887 | 100 | 7.0686 | 9.4248 | 0.75 | 5.0348 | 0 | 1 | 0.39362 | 0.39362 | 32.1461
[13 empty] | Total | 32.1461

## HL 24.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 24 | 37.1361 | 140 | 7.0686 | 9.4248 | 0.75 | 5.2537 | 0 | 0.25 | 0.10715 | 0.10715 | 0.10715
| 36 | 30" X 36" Increaser | 24 | 37.1361 | 140 | 7.0686 | 9.4248 | 0.75 | 5.2537 | 0 | 0.25 | 0.10715 | 0.10715 | 0.21429
1320 | 36 | Pipe | 24 | 37.1361 | 140 | 7.0686 | 9.4248 | 0.75 | 5.2537 | 2.5519 |  | 0 | 2.5519 | 2.7662
| 36 | 90 Deg Bend | 24 | 37.1361 | 140 | 7.0686 | 9.4248 | 0.75 | 5.2537 | 0 | 0.2 | 0.085717 | 0.085717 | 2.8519
1320 | 36 | Pipe | 24 | 37.1361 | 140 | 7.0686 | 9.4248 | 0.75 | 5.2537 | 2.5519 |  | 0 | 2.5519 | 5.4038
| 36 | 45 Deg Bend | 24 | 37.1361 | 140 | 7.0686 | 9.4248 | 0.75 | 5.2537 | 0 | 0.4 | 0.17143 | 0.17143 | 5.5753
1320 | 36 | Pipe | 24 | 37.1361 | 140 | 7.0686 | 9.4248 | 0.75 | 5.2537 | 2.5519 |  | 0 | 2.5519 | 8.1272
| 36 | 45 Deg Bend | 24 | 37.1361 | 140 | 7.0686 | 9.4248 | 0.75 | 5.2537 | 0 | 0.4 | 0.17143 | 0.17143 | 8.2986
1320 | 36 | Pipe | 24 | 37.1361 | 140 | 7.0686 | 9.4248 | 0.75 | 5.2537 | 2.5519 |  | 0 | 2.5519 | 10.8505
| 36 | 45 Deg Bend | 24 | 37.1361 | 140 | 7.0686 | 9.4248 | 0.75 | 5.2537 | 0 | 0.4 | 0.17143 | 0.17143 | 11.022
1320 | 36 | Pipe | 24 | 37.1361 | 140 | 7.0686 | 9.4248 | 0.75 | 5.2537 | 2.5519 |  | 0 | 2.5519 | 13.5739
| 36 | 45 Deg Bend | 24 | 37.1361 | 140 | 7.0686 | 9.4248 | 0.75 | 5.2537 | 0 | 0.4 | 0.17143 | 0.17143 | 13.7453
1320 | 36 | Pipe | 24 | 37.1361 | 140 | 7.0686 | 9.4248 | 0.75 | 5.2537 | 2.5519 |  | 0 | 2.5519 | 16.2972
| 36 | 90 Deg Bend | 24 | 37.1361 | 140 | 7.0686 | 9.4248 | 0.75 | 5.2537 | 0 | 0.2 | 0.085717 | 0.085717 | 16.3829
1320 | 36 | Pipe | 24 | 37.1361 | 140 | 7.0686 | 9.4248 | 0.75 | 5.2537 | 2.5519 |  | 0 | 2.5519 | 18.9348
| 36 | Exit to Headworks | 24 | 37.1361 | 140 | 7.0686 | 9.4248 | 0.75 | 5.2537 | 0 | 1 | 0.42859 | 0.42859 | 19.3634
[13 empty] | Total | 19.3634
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 24 | 37.1361 | 100 | 7.0686 | 9.4248 | 0.75 | 5.2537 | 0 | 0.25 | 0.10715 | 0.10715 | 0.10715
| 36 | 30" X 36" Increaser | 24 | 37.1361 | 100 | 7.0686 | 9.4248 | 0.75 | 5.2537 | 0 | 0.25 | 0.10715 | 0.10715 | 0.21429
1320 | 36 | Pipe | 24 | 37.1361 | 100 | 7.0686 | 9.4248 | 0.75 | 5.2537 | 4.7556 |  | 0 | 4.7556 | 4.9699
| 36 | 90 Deg Bend | 24 | 37.1361 | 100 | 7.0686 | 9.4248 | 0.75 | 5.2537 | 0 | 0.2 | 0.085717 | 0.085717 | 5.0556
1320 | 36 | Pipe | 24 | 37.1361 | 100 | 7.0686 | 9.4248 | 0.75 | 5.2537 | 4.7556 |  | 0 | 4.7556 | 9.8111
| 36 | 45 Deg Bend | 24 | 37.1361 | 100 | 7.0686 | 9.4248 | 0.75 | 5.2537 | 0 | 0.4 | 0.17143 | 0.17143 | 9.9826
1320 | 36 | Pipe | 24 | 37.1361 | 100 | 7.0686 | 9.4248 | 0.75 | 5.2537 | 4.7556 |  | 0 | 4.7556 | 14.7381
| 36 | 45 Deg Bend | 24 | 37.1361 | 100 | 7.0686 | 9.4248 | 0.75 | 5.2537 | 0 | 0.4 | 0.17143 | 0.17143 | 14.9096
1320 | 36 | Pipe | 24 | 37.1361 | 100 | 7.0686 | 9.4248 | 0.75 | 5.2537 | 4.7556 |  | 0 | 4.7556 | 19.6651
| 36 | 45 Deg Bend | 24 | 37.1361 | 100 | 7.0686 | 9.4248 | 0.75 | 5.2537 | 0 | 0.4 | 0.17143 | 0.17143 | 19.8366
1320 | 36 | Pipe | 24 | 37.1361 | 100 | 7.0686 | 9.4248 | 0.75 | 5.2537 | 4.7556 |  | 0 | 4.7556 | 24.5921
| 36 | 45 Deg Bend | 24 | 37.1361 | 100 | 7.0686 | 9.4248 | 0.75 | 5.2537 | 0 | 0.4 | 0.17143 | 0.17143 | 24.7636
1320 | 36 | Pipe | 24 | 37.1361 | 100 | 7.0686 | 9.4248 | 0.75 | 5.2537 | 4.7556 |  | 0 | 4.7556 | 29.5191
| 36 | 90 Deg Bend | 24 | 37.1361 | 100 | 7.0686 | 9.4248 | 0.75 | 5.2537 | 0 | 0.2 | 0.085717 | 0.085717 | 29.6049
1320 | 36 | Pipe | 24 | 37.1361 | 100 | 7.0686 | 9.4248 | 0.75 | 5.2537 | 4.7556 |  | 0 | 4.7556 | 34.3604
| 36 | Exit to Headworks | 24 | 37.1361 | 100 | 7.0686 | 9.4248 | 0.75 | 5.2537 | 0 | 1 | 0.42859 | 0.42859 | 34.789
[13 empty] | Total | 34.789

## HL 25.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 25 | 38.6834 | 140 | 7.0686 | 9.4248 | 0.75 | 5.4726 | 0 | 0.25 | 0.11626 | 0.11626 | 0.11626
| 36 | 30" X 36" Increaser | 25 | 38.6834 | 140 | 7.0686 | 9.4248 | 0.75 | 5.4726 | 0 | 0.25 | 0.11626 | 0.11626 | 0.23252
1320 | 36 | Pipe | 25 | 38.6834 | 140 | 7.0686 | 9.4248 | 0.75 | 5.4726 | 2.7521 |  | 0 | 2.7521 | 2.9846
| 36 | 90 Deg Bend | 25 | 38.6834 | 140 | 7.0686 | 9.4248 | 0.75 | 5.4726 | 0 | 0.2 | 0.093009 | 0.093009 | 3.0776
1320 | 36 | Pipe | 25 | 38.6834 | 140 | 7.0686 | 9.4248 | 0.75 | 5.4726 | 2.7521 |  | 0 | 2.7521 | 5.8297
| 36 | 45 Deg Bend | 25 | 38.6834 | 140 | 7.0686 | 9.4248 | 0.75 | 5.4726 | 0 | 0.4 | 0.18602 | 0.18602 | 6.0157
1320 | 36 | Pipe | 25 | 38.6834 | 140 | 7.0686 | 9.4248 | 0.75 | 5.4726 | 2.7521 |  | 0 | 2.7521 | 8.7678
| 36 | 45 Deg Bend | 25 | 38.6834 | 140 | 7.0686 | 9.4248 | 0.75 | 5.4726 | 0 | 0.4 | 0.18602 | 0.18602 | 8.9539
1320 | 36 | Pipe | 25 | 38.6834 | 140 | 7.0686 | 9.4248 | 0.75 | 5.4726 | 2.7521 |  | 0 | 2.7521 | 11.706
| 36 | 45 Deg Bend | 25 | 38.6834 | 140 | 7.0686 | 9.4248 | 0.75 | 5.4726 | 0 | 0.4 | 0.18602 | 0.18602 | 11.892
1320 | 36 | Pipe | 25 | 38.6834 | 140 | 7.0686 | 9.4248 | 0.75 | 5.4726 | 2.7521 |  | 0 | 2.7521 | 14.6441
| 36 | 45 Deg Bend | 25 | 38.6834 | 140 | 7.0686 | 9.4248 | 0.75 | 5.4726 | 0 | 0.4 | 0.18602 | 0.18602 | 14.8301
1320 | 36 | Pipe | 25 | 38.6834 | 140 | 7.0686 | 9.4248 | 0.75 | 5.4726 | 2.7521 |  | 0 | 2.7521 | 17.5822
| 36 | 90 Deg Bend | 25 | 38.6834 | 140 | 7.0686 | 9.4248 | 0.75 | 5.4726 | 0 | 0.2 | 0.093009 | 0.093009 | 17.6752
1320 | 36 | Pipe | 25 | 38.6834 | 140 | 7.0686 | 9.4248 | 0.75 | 5.4726 | 2.7521 |  | 0 | 2.7521 | 20.4273
| 36 | Exit to Headworks | 25 | 38.6834 | 140 | 7.0686 | 9.4248 | 0.75 | 5.4726 | 0 | 1 | 0.46505 | 0.46505 | 20.8923
[13 empty] | Total | 20.8923
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 25 | 38.6834 | 100 | 7.0686 | 9.4248 | 0.75 | 5.4726 | 0 | 0.25 | 0.11626 | 0.11626 | 0.11626
| 36 | 30" X 36" Increaser | 25 | 38.6834 | 100 | 7.0686 | 9.4248 | 0.75 | 5.4726 | 0 | 0.25 | 0.11626 | 0.11626 | 0.23252
1320 | 36 | Pipe | 25 | 38.6834 | 100 | 7.0686 | 9.4248 | 0.75 | 5.4726 | 5.1286 |  | 0 | 5.1286 | 5.3611
| 36 | 90 Deg Bend | 25 | 38.6834 | 100 | 7.0686 | 9.4248 | 0.75 | 5.4726 | 0 | 0.2 | 0.093009 | 0.093009 | 5.4542
1320 | 36 | Pipe | 25 | 38.6834 | 100 | 7.0686 | 9.4248 | 0.75 | 5.4726 | 5.1286 |  | 0 | 5.1286 | 10.5828
| 36 | 45 Deg Bend | 25 | 38.6834 | 100 | 7.0686 | 9.4248 | 0.75 | 5.4726 | 0 | 0.4 | 0.18602 | 0.18602 | 10.7688
1320 | 36 | Pipe | 25 | 38.6834 | 100 | 7.0686 | 9.4248 | 0.75 | 5.4726 | 5.1286 |  | 0 | 5.1286 | 15.8974
| 36 | 45 Deg Bend | 25 | 38.6834 | 100 | 7.0686 | 9.4248 | 0.75 | 5.4726 | 0 | 0.4 | 0.18602 | 0.18602 | 16.0834
1320 | 36 | Pipe | 25 | 38.6834 | 100 | 7.0686 | 9.4248 | 0.75 | 5.4726 | 5.1286 |  | 0 | 5.1286 | 21.212
| 36 | 45 Deg Bend | 25 | 38.6834 | 100 | 7.0686 | 9.4248 | 0.75 | 5.4726 | 0 | 0.4 | 0.18602 | 0.18602 | 21.3981
1320 | 36 | Pipe | 25 | 38.6834 | 100 | 7.0686 | 9.4248 | 0.75 | 5.4726 | 5.1286 |  | 0 | 5.1286 | 26.5267
| 36 | 45 Deg Bend | 25 | 38.6834 | 100 | 7.0686 | 9.4248 | 0.75 | 5.4726 | 0 | 0.4 | 0.18602 | 0.18602 | 26.7127
1320 | 36 | Pipe | 25 | 38.6834 | 100 | 7.0686 | 9.4248 | 0.75 | 5.4726 | 5.1286 |  | 0 | 5.1286 | 31.8413
| 36 | 90 Deg Bend | 25 | 38.6834 | 100 | 7.0686 | 9.4248 | 0.75 | 5.4726 | 0 | 0.2 | 0.093009 | 0.093009 | 31.9343
1320 | 36 | Pipe | 25 | 38.6834 | 100 | 7.0686 | 9.4248 | 0.75 | 5.4726 | 5.1286 |  | 0 | 5.1286 | 37.0629
| 36 | Exit to Headworks | 25 | 38.6834 | 100 | 7.0686 | 9.4248 | 0.75 | 5.4726 | 0 | 1 | 0.46505 | 0.46505 | 37.528
[13 empty] | Total | 37.528

## HL 26.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 26 | 40.2307 | 140 | 7.0686 | 9.4248 | 0.75 | 5.6915 | 0 | 0.25 | 0.12575 | 0.12575 | 0.12575
| 36 | 30" X 36" Increaser | 26 | 40.2307 | 140 | 7.0686 | 9.4248 | 0.75 | 5.6915 | 0 | 0.25 | 0.12575 | 0.12575 | 0.2515
1320 | 36 | Pipe | 26 | 40.2307 | 140 | 7.0686 | 9.4248 | 0.75 | 5.6915 | 2.9592 |  | 0 | 2.9592 | 3.2107
| 36 | 90 Deg Bend | 26 | 40.2307 | 140 | 7.0686 | 9.4248 | 0.75 | 5.6915 | 0 | 0.2 | 0.1006 | 0.1006 | 3.3113
1320 | 36 | Pipe | 26 | 40.2307 | 140 | 7.0686 | 9.4248 | 0.75 | 5.6915 | 2.9592 |  | 0 | 2.9592 | 6.2705
| 36 | 45 Deg Bend | 26 | 40.2307 | 140 | 7.0686 | 9.4248 | 0.75 | 5.6915 | 0 | 0.4 | 0.2012 | 0.2012 | 6.4717
1320 | 36 | Pipe | 26 | 40.2307 | 140 | 7.0686 | 9.4248 | 0.75 | 5.6915 | 2.9592 |  | 0 | 2.9592 | 9.4309
| 36 | 45 Deg Bend | 26 | 40.2307 | 140 | 7.0686 | 9.4248 | 0.75 | 5.6915 | 0 | 0.4 | 0.2012 | 0.2012 | 9.6321
1320 | 36 | Pipe | 26 | 40.2307 | 140 | 7.0686 | 9.4248 | 0.75 | 5.6915 | 2.9592 |  | 0 | 2.9592 | 12.5913
| 36 | 45 Deg Bend | 26 | 40.2307 | 140 | 7.0686 | 9.4248 | 0.75 | 5.6915 | 0 | 0.4 | 0.2012 | 0.2012 | 12.7925
1320 | 36 | Pipe | 26 | 40.2307 | 140 | 7.0686 | 9.4248 | 0.75 | 5.6915 | 2.9592 |  | 0 | 2.9592 | 15.7517
| 36 | 45 Deg Bend | 26 | 40.2307 | 140 | 7.0686 | 9.4248 | 0.75 | 5.6915 | 0 | 0.4 | 0.2012 | 0.2012 | 15.9529
1320 | 36 | Pipe | 26 | 40.2307 | 140 | 7.0686 | 9.4248 | 0.75 | 5.6915 | 2.9592 |  | 0 | 2.9592 | 18.9121
| 36 | 90 Deg Bend | 26 | 40.2307 | 140 | 7.0686 | 9.4248 | 0.75 | 5.6915 | 0 | 0.2 | 0.1006 | 0.1006 | 19.0127
1320 | 36 | Pipe | 26 | 40.2307 | 140 | 7.0686 | 9.4248 | 0.75 | 5.6915 | 2.9592 |  | 0 | 2.9592 | 21.9719
| 36 | Exit to Headworks | 26 | 40.2307 | 140 | 7.0686 | 9.4248 | 0.75 | 5.6915 | 0 | 1 | 0.50299 | 0.50299 | 22.4749
[13 empty] | Total | 22.4749
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 26 | 40.2307 | 100 | 7.0686 | 9.4248 | 0.75 | 5.6915 | 0 | 0.25 | 0.12575 | 0.12575 | 0.12575
| 36 | 30" X 36" Increaser | 26 | 40.2307 | 100 | 7.0686 | 9.4248 | 0.75 | 5.6915 | 0 | 0.25 | 0.12575 | 0.12575 | 0.2515
1320 | 36 | Pipe | 26 | 40.2307 | 100 | 7.0686 | 9.4248 | 0.75 | 5.6915 | 5.5146 |  | 0 | 5.5146 | 5.7661
| 36 | 90 Deg Bend | 26 | 40.2307 | 100 | 7.0686 | 9.4248 | 0.75 | 5.6915 | 0 | 0.2 | 0.1006 | 0.1006 | 5.8667
1320 | 36 | Pipe | 26 | 40.2307 | 100 | 7.0686 | 9.4248 | 0.75 | 5.6915 | 5.5146 |  | 0 | 5.5146 | 11.3812
| 36 | 45 Deg Bend | 26 | 40.2307 | 100 | 7.0686 | 9.4248 | 0.75 | 5.6915 | 0 | 0.4 | 0.2012 | 0.2012 | 11.5824
1320 | 36 | Pipe | 26 | 40.2307 | 100 | 7.0686 | 9.4248 | 0.75 | 5.6915 | 5.5146 |  | 0 | 5.5146 | 17.097
| 36 | 45 Deg Bend | 26 | 40.2307 | 100 | 7.0686 | 9.4248 | 0.75 | 5.6915 | 0 | 0.4 | 0.2012 | 0.2012 | 17.2982
1320 | 36 | Pipe | 26 | 40.2307 | 100 | 7.0686 | 9.4248 | 0.75 | 5.6915 | 5.5146 |  | 0 | 5.5146 | 22.8128
| 36 | 45 Deg Bend | 26 | 40.2307 | 100 | 7.0686 | 9.4248 | 0.75 | 5.6915 | 0 | 0.4 | 0.2012 | 0.2012 | 23.014
1320 | 36 | Pipe | 26 | 40.2307 | 100 | 7.0686 | 9.4248 | 0.75 | 5.6915 | 5.5146 |  | 0 | 5.5146 | 28.5286
| 36 | 45 Deg Bend | 26 | 40.2307 | 100 | 7.0686 | 9.4248 | 0.75 | 5.6915 | 0 | 0.4 | 0.2012 | 0.2012 | 28.7298
1320 | 36 | Pipe | 26 | 40.2307 | 100 | 7.0686 | 9.4248 | 0.75 | 5.6915 | 5.5146 |  | 0 | 5.5146 | 34.2443
| 36 | 90 Deg Bend | 26 | 40.2307 | 100 | 7.0686 | 9.4248 | 0.75 | 5.6915 | 0 | 0.2 | 0.1006 | 0.1006 | 34.3449
1320 | 36 | Pipe | 26 | 40.2307 | 100 | 7.0686 | 9.4248 | 0.75 | 5.6915 | 5.5146 |  | 0 | 5.5146 | 39.8595
| 36 | Exit to Headworks | 26 | 40.2307 | 100 | 7.0686 | 9.4248 | 0.75 | 5.6915 | 0 | 1 | 0.50299 | 0.50299 | 40.3625
[13 empty] | Total | 40.3625

## HL 27.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 27 | 41.7781 | 140 | 7.0686 | 9.4248 | 0.75 | 5.9104 | 0 | 0.25 | 0.13561 | 0.13561 | 0.13561
| 36 | 30" X 36" Increaser | 27 | 41.7781 | 140 | 7.0686 | 9.4248 | 0.75 | 5.9104 | 0 | 0.25 | 0.13561 | 0.13561 | 0.27122
1320 | 36 | Pipe | 27 | 41.7781 | 140 | 7.0686 | 9.4248 | 0.75 | 5.9104 | 3.1732 |  | 0 | 3.1732 | 3.4444
| 36 | 90 Deg Bend | 27 | 41.7781 | 140 | 7.0686 | 9.4248 | 0.75 | 5.9104 | 0 | 0.2 | 0.10849 | 0.10849 | 3.5529
1320 | 36 | Pipe | 27 | 41.7781 | 140 | 7.0686 | 9.4248 | 0.75 | 5.9104 | 3.1732 |  | 0 | 3.1732 | 6.7261
| 36 | 45 Deg Bend | 27 | 41.7781 | 140 | 7.0686 | 9.4248 | 0.75 | 5.9104 | 0 | 0.4 | 0.21697 | 0.21697 | 6.9431
1320 | 36 | Pipe | 27 | 41.7781 | 140 | 7.0686 | 9.4248 | 0.75 | 5.9104 | 3.1732 |  | 0 | 3.1732 | 10.1163
| 36 | 45 Deg Bend | 27 | 41.7781 | 140 | 7.0686 | 9.4248 | 0.75 | 5.9104 | 0 | 0.4 | 0.21697 | 0.21697 | 10.3332
1320 | 36 | Pipe | 27 | 41.7781 | 140 | 7.0686 | 9.4248 | 0.75 | 5.9104 | 3.1732 |  | 0 | 3.1732 | 13.5064
| 36 | 45 Deg Bend | 27 | 41.7781 | 140 | 7.0686 | 9.4248 | 0.75 | 5.9104 | 0 | 0.4 | 0.21697 | 0.21697 | 13.7234
1320 | 36 | Pipe | 27 | 41.7781 | 140 | 7.0686 | 9.4248 | 0.75 | 5.9104 | 3.1732 |  | 0 | 3.1732 | 16.8966
| 36 | 45 Deg Bend | 27 | 41.7781 | 140 | 7.0686 | 9.4248 | 0.75 | 5.9104 | 0 | 0.4 | 0.21697 | 0.21697 | 17.1136
1320 | 36 | Pipe | 27 | 41.7781 | 140 | 7.0686 | 9.4248 | 0.75 | 5.9104 | 3.1732 |  | 0 | 3.1732 | 20.2868
| 36 | 90 Deg Bend | 27 | 41.7781 | 140 | 7.0686 | 9.4248 | 0.75 | 5.9104 | 0 | 0.2 | 0.10849 | 0.10849 | 20.3953
1320 | 36 | Pipe | 27 | 41.7781 | 140 | 7.0686 | 9.4248 | 0.75 | 5.9104 | 3.1732 |  | 0 | 3.1732 | 23.5685
| 36 | Exit to Headworks | 27 | 41.7781 | 140 | 7.0686 | 9.4248 | 0.75 | 5.9104 | 0 | 1 | 0.54243 | 0.54243 | 24.1109
[13 empty] | Total | 24.1109
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 27 | 41.7781 | 100 | 7.0686 | 9.4248 | 0.75 | 5.9104 | 0 | 0.25 | 0.13561 | 0.13561 | 0.13561
| 36 | 30" X 36" Increaser | 27 | 41.7781 | 100 | 7.0686 | 9.4248 | 0.75 | 5.9104 | 0 | 0.25 | 0.13561 | 0.13561 | 0.27122
1320 | 36 | Pipe | 27 | 41.7781 | 100 | 7.0686 | 9.4248 | 0.75 | 5.9104 | 5.9134 |  | 0 | 5.9134 | 6.1846
| 36 | 90 Deg Bend | 27 | 41.7781 | 100 | 7.0686 | 9.4248 | 0.75 | 5.9104 | 0 | 0.2 | 0.10849 | 0.10849 | 6.2931
1320 | 36 | Pipe | 27 | 41.7781 | 100 | 7.0686 | 9.4248 | 0.75 | 5.9104 | 5.9134 |  | 0 | 5.9134 | 12.2064
| 36 | 45 Deg Bend | 27 | 41.7781 | 100 | 7.0686 | 9.4248 | 0.75 | 5.9104 | 0 | 0.4 | 0.21697 | 0.21697 | 12.4234
1320 | 36 | Pipe | 27 | 41.7781 | 100 | 7.0686 | 9.4248 | 0.75 | 5.9104 | 5.9134 |  | 0 | 5.9134 | 18.3368
| 36 | 45 Deg Bend | 27 | 41.7781 | 100 | 7.0686 | 9.4248 | 0.75 | 5.9104 | 0 | 0.4 | 0.21697 | 0.21697 | 18.5537
1320 | 36 | Pipe | 27 | 41.7781 | 100 | 7.0686 | 9.4248 | 0.75 | 5.9104 | 5.9134 |  | 0 | 5.9134 | 24.4671
| 36 | 45 Deg Bend | 27 | 41.7781 | 100 | 7.0686 | 9.4248 | 0.75 | 5.9104 | 0 | 0.4 | 0.21697 | 0.21697 | 24.6841
1320 | 36 | Pipe | 27 | 41.7781 | 100 | 7.0686 | 9.4248 | 0.75 | 5.9104 | 5.9134 |  | 0 | 5.9134 | 30.5974
| 36 | 45 Deg Bend | 27 | 41.7781 | 100 | 7.0686 | 9.4248 | 0.75 | 5.9104 | 0 | 0.4 | 0.21697 | 0.21697 | 30.8144
1320 | 36 | Pipe | 27 | 41.7781 | 100 | 7.0686 | 9.4248 | 0.75 | 5.9104 | 5.9134 |  | 0 | 5.9134 | 36.7277
| 36 | 90 Deg Bend | 27 | 41.7781 | 100 | 7.0686 | 9.4248 | 0.75 | 5.9104 | 0 | 0.2 | 0.10849 | 0.10849 | 36.8362
1320 | 36 | Pipe | 27 | 41.7781 | 100 | 7.0686 | 9.4248 | 0.75 | 5.9104 | 5.9134 |  | 0 | 5.9134 | 42.7496
| 36 | Exit to Headworks | 27 | 41.7781 | 100 | 7.0686 | 9.4248 | 0.75 | 5.9104 | 0 | 1 | 0.54243 | 0.54243 | 43.292
[13 empty] | Total | 43.292

## HL 28.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 28 | 43.3254 | 140 | 7.0686 | 9.4248 | 0.75 | 6.1293 | 0 | 0.25 | 0.14584 | 0.14584 | 0.14584
| 36 | 30" X 36" Increaser | 28 | 43.3254 | 140 | 7.0686 | 9.4248 | 0.75 | 6.1293 | 0 | 0.25 | 0.14584 | 0.14584 | 0.29168
1320 | 36 | Pipe | 28 | 43.3254 | 140 | 7.0686 | 9.4248 | 0.75 | 6.1293 | 3.394 |  | 0 | 3.394 | 3.6857
| 36 | 90 Deg Bend | 28 | 43.3254 | 140 | 7.0686 | 9.4248 | 0.75 | 6.1293 | 0 | 0.2 | 0.11667 | 0.11667 | 3.8024
1320 | 36 | Pipe | 28 | 43.3254 | 140 | 7.0686 | 9.4248 | 0.75 | 6.1293 | 3.394 |  | 0 | 3.394 | 7.1964
| 36 | 45 Deg Bend | 28 | 43.3254 | 140 | 7.0686 | 9.4248 | 0.75 | 6.1293 | 0 | 0.4 | 0.23334 | 0.23334 | 7.4298
1320 | 36 | Pipe | 28 | 43.3254 | 140 | 7.0686 | 9.4248 | 0.75 | 6.1293 | 3.394 |  | 0 | 3.394 | 10.8238
| 36 | 45 Deg Bend | 28 | 43.3254 | 140 | 7.0686 | 9.4248 | 0.75 | 6.1293 | 0 | 0.4 | 0.23334 | 0.23334 | 11.0571
1320 | 36 | Pipe | 28 | 43.3254 | 140 | 7.0686 | 9.4248 | 0.75 | 6.1293 | 3.394 |  | 0 | 3.394 | 14.4512
| 36 | 45 Deg Bend | 28 | 43.3254 | 140 | 7.0686 | 9.4248 | 0.75 | 6.1293 | 0 | 0.4 | 0.23334 | 0.23334 | 14.6845
1320 | 36 | Pipe | 28 | 43.3254 | 140 | 7.0686 | 9.4248 | 0.75 | 6.1293 | 3.394 |  | 0 | 3.394 | 18.0786
| 36 | 45 Deg Bend | 28 | 43.3254 | 140 | 7.0686 | 9.4248 | 0.75 | 6.1293 | 0 | 0.4 | 0.23334 | 0.23334 | 18.3119
1320 | 36 | Pipe | 28 | 43.3254 | 140 | 7.0686 | 9.4248 | 0.75 | 6.1293 | 3.394 |  | 0 | 3.394 | 21.7059
| 36 | 90 Deg Bend | 28 | 43.3254 | 140 | 7.0686 | 9.4248 | 0.75 | 6.1293 | 0 | 0.2 | 0.11667 | 0.11667 | 21.8226
1320 | 36 | Pipe | 28 | 43.3254 | 140 | 7.0686 | 9.4248 | 0.75 | 6.1293 | 3.394 |  | 0 | 3.394 | 25.2167
| 36 | Exit to Headworks | 28 | 43.3254 | 140 | 7.0686 | 9.4248 | 0.75 | 6.1293 | 0 | 1 | 0.58335 | 0.58335 | 25.8
[13 empty] | Total | 25.8
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 28 | 43.3254 | 100 | 7.0686 | 9.4248 | 0.75 | 6.1293 | 0 | 0.25 | 0.14584 | 0.14584 | 0.14584
| 36 | 30" X 36" Increaser | 28 | 43.3254 | 100 | 7.0686 | 9.4248 | 0.75 | 6.1293 | 0 | 0.25 | 0.14584 | 0.14584 | 0.29168
1320 | 36 | Pipe | 28 | 43.3254 | 100 | 7.0686 | 9.4248 | 0.75 | 6.1293 | 6.3249 |  | 0 | 6.3249 | 6.6166
| 36 | 90 Deg Bend | 28 | 43.3254 | 100 | 7.0686 | 9.4248 | 0.75 | 6.1293 | 0 | 0.2 | 0.11667 | 0.11667 | 6.7332
1320 | 36 | Pipe | 28 | 43.3254 | 100 | 7.0686 | 9.4248 | 0.75 | 6.1293 | 6.3249 |  | 0 | 6.3249 | 13.0581
| 36 | 45 Deg Bend | 28 | 43.3254 | 100 | 7.0686 | 9.4248 | 0.75 | 6.1293 | 0 | 0.4 | 0.23334 | 0.23334 | 13.2915
1320 | 36 | Pipe | 28 | 43.3254 | 100 | 7.0686 | 9.4248 | 0.75 | 6.1293 | 6.3249 |  | 0 | 6.3249 | 19.6164
| 36 | 45 Deg Bend | 28 | 43.3254 | 100 | 7.0686 | 9.4248 | 0.75 | 6.1293 | 0 | 0.4 | 0.23334 | 0.23334 | 19.8497
1320 | 36 | Pipe | 28 | 43.3254 | 100 | 7.0686 | 9.4248 | 0.75 | 6.1293 | 6.3249 |  | 0 | 6.3249 | 26.1746
| 36 | 45 Deg Bend | 28 | 43.3254 | 100 | 7.0686 | 9.4248 | 0.75 | 6.1293 | 0 | 0.4 | 0.23334 | 0.23334 | 26.408
1320 | 36 | Pipe | 28 | 43.3254 | 100 | 7.0686 | 9.4248 | 0.75 | 6.1293 | 6.3249 |  | 0 | 6.3249 | 32.7329
| 36 | 45 Deg Bend | 28 | 43.3254 | 100 | 7.0686 | 9.4248 | 0.75 | 6.1293 | 0 | 0.4 | 0.23334 | 0.23334 | 32.9662
1320 | 36 | Pipe | 28 | 43.3254 | 100 | 7.0686 | 9.4248 | 0.75 | 6.1293 | 6.3249 |  | 0 | 6.3249 | 39.2911
| 36 | 90 Deg Bend | 28 | 43.3254 | 100 | 7.0686 | 9.4248 | 0.75 | 6.1293 | 0 | 0.2 | 0.11667 | 0.11667 | 39.4078
1320 | 36 | Pipe | 28 | 43.3254 | 100 | 7.0686 | 9.4248 | 0.75 | 6.1293 | 6.3249 |  | 0 | 6.3249 | 45.7327
| 36 | Exit to Headworks | 28 | 43.3254 | 100 | 7.0686 | 9.4248 | 0.75 | 6.1293 | 0 | 1 | 0.58335 | 0.58335 | 46.316
[13 empty] | Total | 46.316

## HL 29.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 29 | 44.8727 | 140 | 7.0686 | 9.4248 | 0.75 | 6.3482 | 0 | 0.25 | 0.15644 | 0.15644 | 0.15644
| 36 | 30" X 36" Increaser | 29 | 44.8727 | 140 | 7.0686 | 9.4248 | 0.75 | 6.3482 | 0 | 0.25 | 0.15644 | 0.15644 | 0.31288
1320 | 36 | Pipe | 29 | 44.8727 | 140 | 7.0686 | 9.4248 | 0.75 | 6.3482 | 3.6217 |  | 0 | 3.6217 | 3.9346
| 36 | 90 Deg Bend | 29 | 44.8727 | 140 | 7.0686 | 9.4248 | 0.75 | 6.3482 | 0 | 0.2 | 0.12515 | 0.12515 | 4.0597
1320 | 36 | Pipe | 29 | 44.8727 | 140 | 7.0686 | 9.4248 | 0.75 | 6.3482 | 3.6217 |  | 0 | 3.6217 | 7.6814
| 36 | 45 Deg Bend | 29 | 44.8727 | 140 | 7.0686 | 9.4248 | 0.75 | 6.3482 | 0 | 0.4 | 0.25031 | 0.25031 | 7.9317
1320 | 36 | Pipe | 29 | 44.8727 | 140 | 7.0686 | 9.4248 | 0.75 | 6.3482 | 3.6217 |  | 0 | 3.6217 | 11.5534
| 36 | 45 Deg Bend | 29 | 44.8727 | 140 | 7.0686 | 9.4248 | 0.75 | 6.3482 | 0 | 0.4 | 0.25031 | 0.25031 | 11.8037
1320 | 36 | Pipe | 29 | 44.8727 | 140 | 7.0686 | 9.4248 | 0.75 | 6.3482 | 3.6217 |  | 0 | 3.6217 | 15.4254
| 36 | 45 Deg Bend | 29 | 44.8727 | 140 | 7.0686 | 9.4248 | 0.75 | 6.3482 | 0 | 0.4 | 0.25031 | 0.25031 | 15.6757
1320 | 36 | Pipe | 29 | 44.8727 | 140 | 7.0686 | 9.4248 | 0.75 | 6.3482 | 3.6217 |  | 0 | 3.6217 | 19.2974
| 36 | 45 Deg Bend | 29 | 44.8727 | 140 | 7.0686 | 9.4248 | 0.75 | 6.3482 | 0 | 0.4 | 0.25031 | 0.25031 | 19.5477
1320 | 36 | Pipe | 29 | 44.8727 | 140 | 7.0686 | 9.4248 | 0.75 | 6.3482 | 3.6217 |  | 0 | 3.6217 | 23.1694
| 36 | 90 Deg Bend | 29 | 44.8727 | 140 | 7.0686 | 9.4248 | 0.75 | 6.3482 | 0 | 0.2 | 0.12515 | 0.12515 | 23.2945
1320 | 36 | Pipe | 29 | 44.8727 | 140 | 7.0686 | 9.4248 | 0.75 | 6.3482 | 3.6217 |  | 0 | 3.6217 | 26.9162
| 36 | Exit to Headworks | 29 | 44.8727 | 140 | 7.0686 | 9.4248 | 0.75 | 6.3482 | 0 | 1 | 0.62577 | 0.62577 | 27.542
[13 empty] | Total | 27.542
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 29 | 44.8727 | 100 | 7.0686 | 9.4248 | 0.75 | 6.3482 | 0 | 0.25 | 0.15644 | 0.15644 | 0.15644
| 36 | 30" X 36" Increaser | 29 | 44.8727 | 100 | 7.0686 | 9.4248 | 0.75 | 6.3482 | 0 | 0.25 | 0.15644 | 0.15644 | 0.31288
1320 | 36 | Pipe | 29 | 44.8727 | 100 | 7.0686 | 9.4248 | 0.75 | 6.3482 | 6.7491 |  | 0 | 6.7491 | 7.062
| 36 | 90 Deg Bend | 29 | 44.8727 | 100 | 7.0686 | 9.4248 | 0.75 | 6.3482 | 0 | 0.2 | 0.12515 | 0.12515 | 7.1872
1320 | 36 | Pipe | 29 | 44.8727 | 100 | 7.0686 | 9.4248 | 0.75 | 6.3482 | 6.7491 |  | 0 | 6.7491 | 13.9363
| 36 | 45 Deg Bend | 29 | 44.8727 | 100 | 7.0686 | 9.4248 | 0.75 | 6.3482 | 0 | 0.4 | 0.25031 | 0.25031 | 14.1866
1320 | 36 | Pipe | 29 | 44.8727 | 100 | 7.0686 | 9.4248 | 0.75 | 6.3482 | 6.7491 |  | 0 | 6.7491 | 20.9357
| 36 | 45 Deg Bend | 29 | 44.8727 | 100 | 7.0686 | 9.4248 | 0.75 | 6.3482 | 0 | 0.4 | 0.25031 | 0.25031 | 21.186
1320 | 36 | Pipe | 29 | 44.8727 | 100 | 7.0686 | 9.4248 | 0.75 | 6.3482 | 6.7491 |  | 0 | 6.7491 | 27.9352
| 36 | 45 Deg Bend | 29 | 44.8727 | 100 | 7.0686 | 9.4248 | 0.75 | 6.3482 | 0 | 0.4 | 0.25031 | 0.25031 | 28.1855
1320 | 36 | Pipe | 29 | 44.8727 | 100 | 7.0686 | 9.4248 | 0.75 | 6.3482 | 6.7491 |  | 0 | 6.7491 | 34.9346
| 36 | 45 Deg Bend | 29 | 44.8727 | 100 | 7.0686 | 9.4248 | 0.75 | 6.3482 | 0 | 0.4 | 0.25031 | 0.25031 | 35.1849
1320 | 36 | Pipe | 29 | 44.8727 | 100 | 7.0686 | 9.4248 | 0.75 | 6.3482 | 6.7491 |  | 0 | 6.7491 | 41.934
| 36 | 90 Deg Bend | 29 | 44.8727 | 100 | 7.0686 | 9.4248 | 0.75 | 6.3482 | 0 | 0.2 | 0.12515 | 0.12515 | 42.0592
1320 | 36 | Pipe | 29 | 44.8727 | 100 | 7.0686 | 9.4248 | 0.75 | 6.3482 | 6.7491 |  | 0 | 6.7491 | 48.8083
| 36 | Exit to Headworks | 29 | 44.8727 | 100 | 7.0686 | 9.4248 | 0.75 | 6.3482 | 0 | 1 | 0.62577 | 0.62577 | 49.4341
[13 empty] | Total | 49.4341

## HL 30.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 30 | 46.4201 | 140 | 7.0686 | 9.4248 | 0.75 | 6.5671 | 0 | 0.25 | 0.16742 | 0.16742 | 0.16742
| 36 | 30" X 36" Increaser | 30 | 46.4201 | 140 | 7.0686 | 9.4248 | 0.75 | 6.5671 | 0 | 0.25 | 0.16742 | 0.16742 | 0.33483
1320 | 36 | Pipe | 30 | 46.4201 | 140 | 7.0686 | 9.4248 | 0.75 | 6.5671 | 3.8561 |  | 0 | 3.8561 | 4.1909
| 36 | 90 Deg Bend | 30 | 46.4201 | 140 | 7.0686 | 9.4248 | 0.75 | 6.5671 | 0 | 0.2 | 0.13393 | 0.13393 | 4.3249
1320 | 36 | Pipe | 30 | 46.4201 | 140 | 7.0686 | 9.4248 | 0.75 | 6.5671 | 3.8561 |  | 0 | 3.8561 | 8.181
| 36 | 45 Deg Bend | 30 | 46.4201 | 140 | 7.0686 | 9.4248 | 0.75 | 6.5671 | 0 | 0.4 | 0.26787 | 0.26787 | 8.4488
1320 | 36 | Pipe | 30 | 46.4201 | 140 | 7.0686 | 9.4248 | 0.75 | 6.5671 | 3.8561 |  | 0 | 3.8561 | 12.3049
| 36 | 45 Deg Bend | 30 | 46.4201 | 140 | 7.0686 | 9.4248 | 0.75 | 6.5671 | 0 | 0.4 | 0.26787 | 0.26787 | 12.5728
1320 | 36 | Pipe | 30 | 46.4201 | 140 | 7.0686 | 9.4248 | 0.75 | 6.5671 | 3.8561 |  | 0 | 3.8561 | 16.4289
| 36 | 45 Deg Bend | 30 | 46.4201 | 140 | 7.0686 | 9.4248 | 0.75 | 6.5671 | 0 | 0.4 | 0.26787 | 0.26787 | 16.6968
1320 | 36 | Pipe | 30 | 46.4201 | 140 | 7.0686 | 9.4248 | 0.75 | 6.5671 | 3.8561 |  | 0 | 3.8561 | 20.5529
| 36 | 45 Deg Bend | 30 | 46.4201 | 140 | 7.0686 | 9.4248 | 0.75 | 6.5671 | 0 | 0.4 | 0.26787 | 0.26787 | 20.8208
1320 | 36 | Pipe | 30 | 46.4201 | 140 | 7.0686 | 9.4248 | 0.75 | 6.5671 | 3.8561 |  | 0 | 3.8561 | 24.6769
| 36 | 90 Deg Bend | 30 | 46.4201 | 140 | 7.0686 | 9.4248 | 0.75 | 6.5671 | 0 | 0.2 | 0.13393 | 0.13393 | 24.8108
1320 | 36 | Pipe | 30 | 46.4201 | 140 | 7.0686 | 9.4248 | 0.75 | 6.5671 | 3.8561 |  | 0 | 3.8561 | 28.6669
| 36 | Exit to Headworks | 30 | 46.4201 | 140 | 7.0686 | 9.4248 | 0.75 | 6.5671 | 0 | 1 | 0.66967 | 0.66967 | 29.3366
[13 empty] | Total | 29.3366
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 30 | 46.4201 | 100 | 7.0686 | 9.4248 | 0.75 | 6.5671 | 0 | 0.25 | 0.16742 | 0.16742 | 0.16742
| 36 | 30" X 36" Increaser | 30 | 46.4201 | 100 | 7.0686 | 9.4248 | 0.75 | 6.5671 | 0 | 0.25 | 0.16742 | 0.16742 | 0.33483
1320 | 36 | Pipe | 30 | 46.4201 | 100 | 7.0686 | 9.4248 | 0.75 | 6.5671 | 7.186 |  | 0 | 7.186 | 7.5208
| 36 | 90 Deg Bend | 30 | 46.4201 | 100 | 7.0686 | 9.4248 | 0.75 | 6.5671 | 0 | 0.2 | 0.13393 | 0.13393 | 7.6547
1320 | 36 | Pipe | 30 | 46.4201 | 100 | 7.0686 | 9.4248 | 0.75 | 6.5671 | 7.186 |  | 0 | 7.186 | 14.8407
| 36 | 45 Deg Bend | 30 | 46.4201 | 100 | 7.0686 | 9.4248 | 0.75 | 6.5671 | 0 | 0.4 | 0.26787 | 0.26787 | 15.1086
1320 | 36 | Pipe | 30 | 46.4201 | 100 | 7.0686 | 9.4248 | 0.75 | 6.5671 | 7.186 |  | 0 | 7.186 | 22.2946
| 36 | 45 Deg Bend | 30 | 46.4201 | 100 | 7.0686 | 9.4248 | 0.75 | 6.5671 | 0 | 0.4 | 0.26787 | 0.26787 | 22.5624
1320 | 36 | Pipe | 30 | 46.4201 | 100 | 7.0686 | 9.4248 | 0.75 | 6.5671 | 7.186 |  | 0 | 7.186 | 29.7484
| 36 | 45 Deg Bend | 30 | 46.4201 | 100 | 7.0686 | 9.4248 | 0.75 | 6.5671 | 0 | 0.4 | 0.26787 | 0.26787 | 30.0163
1320 | 36 | Pipe | 30 | 46.4201 | 100 | 7.0686 | 9.4248 | 0.75 | 6.5671 | 7.186 |  | 0 | 7.186 | 37.2022
| 36 | 45 Deg Bend | 30 | 46.4201 | 100 | 7.0686 | 9.4248 | 0.75 | 6.5671 | 0 | 0.4 | 0.26787 | 0.26787 | 37.4701
1320 | 36 | Pipe | 30 | 46.4201 | 100 | 7.0686 | 9.4248 | 0.75 | 6.5671 | 7.186 |  | 0 | 7.186 | 44.6561
| 36 | 90 Deg Bend | 30 | 46.4201 | 100 | 7.0686 | 9.4248 | 0.75 | 6.5671 | 0 | 0.2 | 0.13393 | 0.13393 | 44.79
1320 | 36 | Pipe | 30 | 46.4201 | 100 | 7.0686 | 9.4248 | 0.75 | 6.5671 | 7.186 |  | 0 | 7.186 | 51.976
| 36 | Exit to Headworks | 30 | 46.4201 | 100 | 7.0686 | 9.4248 | 0.75 | 6.5671 | 0 | 1 | 0.66967 | 0.66967 | 52.6457
[13 empty] | Total | 52.6457

## HL 31.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 31 | 47.9674 | 140 | 7.0686 | 9.4248 | 0.75 | 6.786 | 0 | 0.25 | 0.17876 | 0.17876 | 0.17876
| 36 | 30" X 36" Increaser | 31 | 47.9674 | 140 | 7.0686 | 9.4248 | 0.75 | 6.786 | 0 | 0.25 | 0.17876 | 0.17876 | 0.35753
1320 | 36 | Pipe | 31 | 47.9674 | 140 | 7.0686 | 9.4248 | 0.75 | 6.786 | 4.0973 |  | 0 | 4.0973 | 4.4548
| 36 | 90 Deg Bend | 31 | 47.9674 | 140 | 7.0686 | 9.4248 | 0.75 | 6.786 | 0 | 0.2 | 0.14301 | 0.14301 | 4.5978
1320 | 36 | Pipe | 31 | 47.9674 | 140 | 7.0686 | 9.4248 | 0.75 | 6.786 | 4.0973 |  | 0 | 4.0973 | 8.6951
| 36 | 45 Deg Bend | 31 | 47.9674 | 140 | 7.0686 | 9.4248 | 0.75 | 6.786 | 0 | 0.4 | 0.28602 | 0.28602 | 8.9811
1320 | 36 | Pipe | 31 | 47.9674 | 140 | 7.0686 | 9.4248 | 0.75 | 6.786 | 4.0973 |  | 0 | 4.0973 | 13.0783
| 36 | 45 Deg Bend | 31 | 47.9674 | 140 | 7.0686 | 9.4248 | 0.75 | 6.786 | 0 | 0.4 | 0.28602 | 0.28602 | 13.3644
1320 | 36 | Pipe | 31 | 47.9674 | 140 | 7.0686 | 9.4248 | 0.75 | 6.786 | 4.0973 |  | 0 | 4.0973 | 17.4616
| 36 | 45 Deg Bend | 31 | 47.9674 | 140 | 7.0686 | 9.4248 | 0.75 | 6.786 | 0 | 0.4 | 0.28602 | 0.28602 | 17.7476
1320 | 36 | Pipe | 31 | 47.9674 | 140 | 7.0686 | 9.4248 | 0.75 | 6.786 | 4.0973 |  | 0 | 4.0973 | 21.8449
| 36 | 45 Deg Bend | 31 | 47.9674 | 140 | 7.0686 | 9.4248 | 0.75 | 6.786 | 0 | 0.4 | 0.28602 | 0.28602 | 22.1309
1320 | 36 | Pipe | 31 | 47.9674 | 140 | 7.0686 | 9.4248 | 0.75 | 6.786 | 4.0973 |  | 0 | 4.0973 | 26.2282
| 36 | 90 Deg Bend | 31 | 47.9674 | 140 | 7.0686 | 9.4248 | 0.75 | 6.786 | 0 | 0.2 | 0.14301 | 0.14301 | 26.3712
1320 | 36 | Pipe | 31 | 47.9674 | 140 | 7.0686 | 9.4248 | 0.75 | 6.786 | 4.0973 |  | 0 | 4.0973 | 30.4685
| 36 | Exit to Headworks | 31 | 47.9674 | 140 | 7.0686 | 9.4248 | 0.75 | 6.786 | 0 | 1 | 0.71506 | 0.71506 | 31.1835
[13 empty] | Total | 31.1835
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 31 | 47.9674 | 100 | 7.0686 | 9.4248 | 0.75 | 6.786 | 0 | 0.25 | 0.17876 | 0.17876 | 0.17876
| 36 | 30" X 36" Increaser | 31 | 47.9674 | 100 | 7.0686 | 9.4248 | 0.75 | 6.786 | 0 | 0.25 | 0.17876 | 0.17876 | 0.35753
1320 | 36 | Pipe | 31 | 47.9674 | 100 | 7.0686 | 9.4248 | 0.75 | 6.786 | 7.6354 |  | 0 | 7.6354 | 7.9929
| 36 | 90 Deg Bend | 31 | 47.9674 | 100 | 7.0686 | 9.4248 | 0.75 | 6.786 | 0 | 0.2 | 0.14301 | 0.14301 | 8.1359
1320 | 36 | Pipe | 31 | 47.9674 | 100 | 7.0686 | 9.4248 | 0.75 | 6.786 | 7.6354 |  | 0 | 7.6354 | 15.7713
| 36 | 45 Deg Bend | 31 | 47.9674 | 100 | 7.0686 | 9.4248 | 0.75 | 6.786 | 0 | 0.4 | 0.28602 | 0.28602 | 16.0573
1320 | 36 | Pipe | 31 | 47.9674 | 100 | 7.0686 | 9.4248 | 0.75 | 6.786 | 7.6354 |  | 0 | 7.6354 | 23.6927
| 36 | 45 Deg Bend | 31 | 47.9674 | 100 | 7.0686 | 9.4248 | 0.75 | 6.786 | 0 | 0.4 | 0.28602 | 0.28602 | 23.9787
1320 | 36 | Pipe | 31 | 47.9674 | 100 | 7.0686 | 9.4248 | 0.75 | 6.786 | 7.6354 |  | 0 | 7.6354 | 31.6141
| 36 | 45 Deg Bend | 31 | 47.9674 | 100 | 7.0686 | 9.4248 | 0.75 | 6.786 | 0 | 0.4 | 0.28602 | 0.28602 | 31.9001
1320 | 36 | Pipe | 31 | 47.9674 | 100 | 7.0686 | 9.4248 | 0.75 | 6.786 | 7.6354 |  | 0 | 7.6354 | 39.5355
| 36 | 45 Deg Bend | 31 | 47.9674 | 100 | 7.0686 | 9.4248 | 0.75 | 6.786 | 0 | 0.4 | 0.28602 | 0.28602 | 39.8215
1320 | 36 | Pipe | 31 | 47.9674 | 100 | 7.0686 | 9.4248 | 0.75 | 6.786 | 7.6354 |  | 0 | 7.6354 | 47.4569
| 36 | 90 Deg Bend | 31 | 47.9674 | 100 | 7.0686 | 9.4248 | 0.75 | 6.786 | 0 | 0.2 | 0.14301 | 0.14301 | 47.5999
1320 | 36 | Pipe | 31 | 47.9674 | 100 | 7.0686 | 9.4248 | 0.75 | 6.786 | 7.6354 |  | 0 | 7.6354 | 55.2353
| 36 | Exit to Headworks | 31 | 47.9674 | 100 | 7.0686 | 9.4248 | 0.75 | 6.786 | 0 | 1 | 0.71506 | 0.71506 | 55.9503
[13 empty] | Total | 55.9503

## HL 32.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 32 | 49.5148 | 140 | 7.0686 | 9.4248 | 0.75 | 7.0049 | 0 | 0.25 | 0.19048 | 0.19048 | 0.19048
| 36 | 30" X 36" Increaser | 32 | 49.5148 | 140 | 7.0686 | 9.4248 | 0.75 | 7.0049 | 0 | 0.25 | 0.19048 | 0.19048 | 0.38097
1320 | 36 | Pipe | 32 | 49.5148 | 140 | 7.0686 | 9.4248 | 0.75 | 7.0049 | 4.3451 |  | 0 | 4.3451 | 4.7261
| 36 | 90 Deg Bend | 32 | 49.5148 | 140 | 7.0686 | 9.4248 | 0.75 | 7.0049 | 0 | 0.2 | 0.15239 | 0.15239 | 4.8785
1320 | 36 | Pipe | 32 | 49.5148 | 140 | 7.0686 | 9.4248 | 0.75 | 7.0049 | 4.3451 |  | 0 | 4.3451 | 9.2236
| 36 | 45 Deg Bend | 32 | 49.5148 | 140 | 7.0686 | 9.4248 | 0.75 | 7.0049 | 0 | 0.4 | 0.30477 | 0.30477 | 9.5284
1320 | 36 | Pipe | 32 | 49.5148 | 140 | 7.0686 | 9.4248 | 0.75 | 7.0049 | 4.3451 |  | 0 | 4.3451 | 13.8735
| 36 | 45 Deg Bend | 32 | 49.5148 | 140 | 7.0686 | 9.4248 | 0.75 | 7.0049 | 0 | 0.4 | 0.30477 | 0.30477 | 14.1783
1320 | 36 | Pipe | 32 | 49.5148 | 140 | 7.0686 | 9.4248 | 0.75 | 7.0049 | 4.3451 |  | 0 | 4.3451 | 18.5234
| 36 | 45 Deg Bend | 32 | 49.5148 | 140 | 7.0686 | 9.4248 | 0.75 | 7.0049 | 0 | 0.4 | 0.30477 | 0.30477 | 18.8282
1320 | 36 | Pipe | 32 | 49.5148 | 140 | 7.0686 | 9.4248 | 0.75 | 7.0049 | 4.3451 |  | 0 | 4.3451 | 23.1733
| 36 | 45 Deg Bend | 32 | 49.5148 | 140 | 7.0686 | 9.4248 | 0.75 | 7.0049 | 0 | 0.4 | 0.30477 | 0.30477 | 23.4781
1320 | 36 | Pipe | 32 | 49.5148 | 140 | 7.0686 | 9.4248 | 0.75 | 7.0049 | 4.3451 |  | 0 | 4.3451 | 27.8232
| 36 | 90 Deg Bend | 32 | 49.5148 | 140 | 7.0686 | 9.4248 | 0.75 | 7.0049 | 0 | 0.2 | 0.15239 | 0.15239 | 27.9756
1320 | 36 | Pipe | 32 | 49.5148 | 140 | 7.0686 | 9.4248 | 0.75 | 7.0049 | 4.3451 |  | 0 | 4.3451 | 32.3207
| 36 | Exit to Headworks | 32 | 49.5148 | 140 | 7.0686 | 9.4248 | 0.75 | 7.0049 | 0 | 1 | 0.76193 | 0.76193 | 33.0826
[13 empty] | Total | 33.0826
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 32 | 49.5148 | 100 | 7.0686 | 9.4248 | 0.75 | 7.0049 | 0 | 0.25 | 0.19048 | 0.19048 | 0.19048
| 36 | 30" X 36" Increaser | 32 | 49.5148 | 100 | 7.0686 | 9.4248 | 0.75 | 7.0049 | 0 | 0.25 | 0.19048 | 0.19048 | 0.38097
1320 | 36 | Pipe | 32 | 49.5148 | 100 | 7.0686 | 9.4248 | 0.75 | 7.0049 | 8.0973 |  | 0 | 8.0973 | 8.4782
| 36 | 90 Deg Bend | 32 | 49.5148 | 100 | 7.0686 | 9.4248 | 0.75 | 7.0049 | 0 | 0.2 | 0.15239 | 0.15239 | 8.6306
1320 | 36 | Pipe | 32 | 49.5148 | 100 | 7.0686 | 9.4248 | 0.75 | 7.0049 | 8.0973 |  | 0 | 8.0973 | 16.7279
| 36 | 45 Deg Bend | 32 | 49.5148 | 100 | 7.0686 | 9.4248 | 0.75 | 7.0049 | 0 | 0.4 | 0.30477 | 0.30477 | 17.0327
1320 | 36 | Pipe | 32 | 49.5148 | 100 | 7.0686 | 9.4248 | 0.75 | 7.0049 | 8.0973 |  | 0 | 8.0973 | 25.1299
| 36 | 45 Deg Bend | 32 | 49.5148 | 100 | 7.0686 | 9.4248 | 0.75 | 7.0049 | 0 | 0.4 | 0.30477 | 0.30477 | 25.4347
1320 | 36 | Pipe | 32 | 49.5148 | 100 | 7.0686 | 9.4248 | 0.75 | 7.0049 | 8.0973 |  | 0 | 8.0973 | 33.532
| 36 | 45 Deg Bend | 32 | 49.5148 | 100 | 7.0686 | 9.4248 | 0.75 | 7.0049 | 0 | 0.4 | 0.30477 | 0.30477 | 33.8368
1320 | 36 | Pipe | 32 | 49.5148 | 100 | 7.0686 | 9.4248 | 0.75 | 7.0049 | 8.0973 |  | 0 | 8.0973 | 41.934
| 36 | 45 Deg Bend | 32 | 49.5148 | 100 | 7.0686 | 9.4248 | 0.75 | 7.0049 | 0 | 0.4 | 0.30477 | 0.30477 | 42.2388
1320 | 36 | Pipe | 32 | 49.5148 | 100 | 7.0686 | 9.4248 | 0.75 | 7.0049 | 8.0973 |  | 0 | 8.0973 | 50.3361
| 36 | 90 Deg Bend | 32 | 49.5148 | 100 | 7.0686 | 9.4248 | 0.75 | 7.0049 | 0 | 0.2 | 0.15239 | 0.15239 | 50.4885
1320 | 36 | Pipe | 32 | 49.5148 | 100 | 7.0686 | 9.4248 | 0.75 | 7.0049 | 8.0973 |  | 0 | 8.0973 | 58.5857
| 36 | Exit to Headworks | 32 | 49.5148 | 100 | 7.0686 | 9.4248 | 0.75 | 7.0049 | 0 | 1 | 0.76193 | 0.76193 | 59.3477
[13 empty] | Total | 59.3477

## HL 33.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 33 | 51.0621 | 140 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 0 | 0.25 | 0.20257 | 0.20257 | 0.20257
| 36 | 30" X 36" Increaser | 33 | 51.0621 | 140 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 0 | 0.25 | 0.20257 | 0.20257 | 0.40515
1320 | 36 | Pipe | 33 | 51.0621 | 140 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 4.5997 |  | 0 | 4.5997 | 5.0048
| 36 | 90 Deg Bend | 33 | 51.0621 | 140 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 0 | 0.2 | 0.16206 | 0.16206 | 5.1669
1320 | 36 | Pipe | 33 | 51.0621 | 140 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 4.5997 |  | 0 | 4.5997 | 9.7665
| 36 | 45 Deg Bend | 33 | 51.0621 | 140 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 0 | 0.4 | 0.32412 | 0.32412 | 10.0906
1320 | 36 | Pipe | 33 | 51.0621 | 140 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 4.5997 |  | 0 | 4.5997 | 14.6903
| 36 | 45 Deg Bend | 33 | 51.0621 | 140 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 0 | 0.4 | 0.32412 | 0.32412 | 15.0144
1320 | 36 | Pipe | 33 | 51.0621 | 140 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 4.5997 |  | 0 | 4.5997 | 19.6141
| 36 | 45 Deg Bend | 33 | 51.0621 | 140 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 0 | 0.4 | 0.32412 | 0.32412 | 19.9382
1320 | 36 | Pipe | 33 | 51.0621 | 140 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 4.5997 |  | 0 | 4.5997 | 24.5378
| 36 | 45 Deg Bend | 33 | 51.0621 | 140 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 0 | 0.4 | 0.32412 | 0.32412 | 24.862
1320 | 36 | Pipe | 33 | 51.0621 | 140 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 4.5997 |  | 0 | 4.5997 | 29.4616
| 36 | 90 Deg Bend | 33 | 51.0621 | 140 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 0 | 0.2 | 0.16206 | 0.16206 | 29.6237
1320 | 36 | Pipe | 33 | 51.0621 | 140 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 4.5997 |  | 0 | 4.5997 | 34.2233
| 36 | Exit to Headworks | 33 | 51.0621 | 140 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 0 | 1 | 0.8103 | 0.8103 | 35.0336
[13 empty] | Total | 35.0336
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 33 | 51.0621 | 100 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 0 | 0.25 | 0.20257 | 0.20257 | 0.20257
| 36 | 30" X 36" Increaser | 33 | 51.0621 | 100 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 0 | 0.25 | 0.20257 | 0.20257 | 0.40515
1320 | 36 | Pipe | 33 | 51.0621 | 100 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 8.5716 |  | 0 | 8.5716 | 8.9768
| 36 | 90 Deg Bend | 33 | 51.0621 | 100 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 0 | 0.2 | 0.16206 | 0.16206 | 9.1388
1320 | 36 | Pipe | 33 | 51.0621 | 100 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 8.5716 |  | 0 | 8.5716 | 17.7104
| 36 | 45 Deg Bend | 33 | 51.0621 | 100 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 0 | 0.4 | 0.32412 | 0.32412 | 18.0345
1320 | 36 | Pipe | 33 | 51.0621 | 100 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 8.5716 |  | 0 | 8.5716 | 26.6061
| 36 | 45 Deg Bend | 33 | 51.0621 | 100 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 0 | 0.4 | 0.32412 | 0.32412 | 26.9303
1320 | 36 | Pipe | 33 | 51.0621 | 100 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 8.5716 |  | 0 | 8.5716 | 35.5019
| 36 | 45 Deg Bend | 33 | 51.0621 | 100 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 0 | 0.4 | 0.32412 | 0.32412 | 35.826
1320 | 36 | Pipe | 33 | 51.0621 | 100 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 8.5716 |  | 0 | 8.5716 | 44.3976
| 36 | 45 Deg Bend | 33 | 51.0621 | 100 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 0 | 0.4 | 0.32412 | 0.32412 | 44.7217
1320 | 36 | Pipe | 33 | 51.0621 | 100 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 8.5716 |  | 0 | 8.5716 | 53.2933
| 36 | 90 Deg Bend | 33 | 51.0621 | 100 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 0 | 0.2 | 0.16206 | 0.16206 | 53.4554
1320 | 36 | Pipe | 33 | 51.0621 | 100 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 8.5716 |  | 0 | 8.5716 | 62.027
| 36 | Exit to Headworks | 33 | 51.0621 | 100 | 7.0686 | 9.4248 | 0.75 | 7.2238 | 0 | 1 | 0.8103 | 0.8103 | 62.8373
[13 empty] | Total | 62.8373

## HL 34.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 34 | 52.6094 | 140 | 7.0686 | 9.4248 | 0.75 | 7.4427 | 0 | 0.25 | 0.21504 | 0.21504 | 0.21504
| 36 | 30" X 36" Increaser | 34 | 52.6094 | 140 | 7.0686 | 9.4248 | 0.75 | 7.4427 | 0 | 0.25 | 0.21504 | 0.21504 | 0.43008
1320 | 36 | Pipe | 34 | 52.6094 | 140 | 7.0686 | 9.4248 | 0.75 | 7.4427 | 4.8608 |  | 0 | 4.8608 | 5.2909
| 36 | 90 Deg Bend | 34 | 52.6094 | 140 | 7.0686 | 9.4248 | 0.75 | 7.4427 | 0 | 0.2 | 0.17203 | 0.17203 | 5.4629
1320 | 36 | Pipe | 34 | 52.6094 | 140 | 7.0686 | 9.4248 | 0.75 | 7.4427 | 4.8608 |  | 0 | 4.8608 | 10.3238
| 36 | 45 Deg Bend | 34 | 52.6094 | 140 | 7.0686 | 9.4248 | 0.75 | 7.4427 | 0 | 0.4 | 0.34406 | 0.34406 | 10.6678
1320 | 36 | Pipe | 34 | 52.6094 | 140 | 7.0686 | 9.4248 | 0.75 | 7.4427 | 4.8608 |  | 0 | 4.8608 | 15.5287
| 36 | 45 Deg Bend | 34 | 52.6094 | 140 | 7.0686 | 9.4248 | 0.75 | 7.4427 | 0 | 0.4 | 0.34406 | 0.34406 | 15.8727
1320 | 36 | Pipe | 34 | 52.6094 | 140 | 7.0686 | 9.4248 | 0.75 | 7.4427 | 4.8608 |  | 0 | 4.8608 | 20.7335
| 36 | 45 Deg Bend | 34 | 52.6094 | 140 | 7.0686 | 9.4248 | 0.75 | 7.4427 | 0 | 0.4 | 0.34406 | 0.34406 | 21.0776
1320 | 36 | Pipe | 34 | 52.6094 | 140 | 7.0686 | 9.4248 | 0.75 | 7.4427 | 4.8608 |  | 0 | 4.8608 | 25.9384
| 36 | 45 Deg Bend | 34 | 52.6094 | 140 | 7.0686 | 9.4248 | 0.75 | 7.4427 | 0 | 0.4 | 0.34406 | 0.34406 | 26.2825
1320 | 36 | Pipe | 34 | 52.6094 | 140 | 7.0686 | 9.4248 | 0.75 | 7.4427 | 4.8608 |  | 0 | 4.8608 | 31.1433
| 36 | 90 Deg Bend | 34 | 52.6094 | 140 | 7.0686 | 9.4248 | 0.75 | 7.4427 | 0 | 0.2 | 0.17203 | 0.17203 | 31.3154
1320 | 36 | Pipe | 34 | 52.6094 | 140 | 7.0686 | 9.4248 | 0.75 | 7.4427 | 4.8608 |  | 0 | 4.8608 | 36.1762
| 36 | Exit to Headworks | 34 | 52.6094 | 140 | 7.0686 | 9.4248 | 0.75 | 7.4427 | 0 | 1 | 0.86015 | 0.86015 | 37.0363
[13 empty] | Total | 37.0363
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 34 | 52.6094 | 100 | 7.0686 | 9.4248 | 0.75 | 7.4427 | 0 | 0.25 | 0.21504 | 0.21504 | 0.21504
| 36 | 30" X 36" Increaser | 34 | 52.6094 | 100 | 7.0686 | 9.4248 | 0.75 | 7.4427 | 0 | 0.25 | 0.21504 | 0.21504 | 0.43008
1320 | 36 | Pipe | 34 | 52.6094 | 100 | 7.0686 | 9.4248 | 0.75 | 7.4427 | 9.0583 |  | 0 | 9.0583 | 9.4884
| 36 | 90 Deg Bend | 34 | 52.6094 | 100 | 7.0686 | 9.4248 | 0.75 | 7.4427 | 0 | 0.2 | 0.17203 | 0.17203 | 9.6604
1320 | 36 | Pipe | 34 | 52.6094 | 100 | 7.0686 | 9.4248 | 0.75 | 7.4427 | 9.0583 |  | 0 | 9.0583 | 18.7187
| 36 | 45 Deg Bend | 34 | 52.6094 | 100 | 7.0686 | 9.4248 | 0.75 | 7.4427 | 0 | 0.4 | 0.34406 | 0.34406 | 19.0628
1320 | 36 | Pipe | 34 | 52.6094 | 100 | 7.0686 | 9.4248 | 0.75 | 7.4427 | 9.0583 |  | 0 | 9.0583 | 28.1211
| 36 | 45 Deg Bend | 34 | 52.6094 | 100 | 7.0686 | 9.4248 | 0.75 | 7.4427 | 0 | 0.4 | 0.34406 | 0.34406 | 28.4652
1320 | 36 | Pipe | 34 | 52.6094 | 100 | 7.0686 | 9.4248 | 0.75 | 7.4427 | 9.0583 |  | 0 | 9.0583 | 37.5235
| 36 | 45 Deg Bend | 34 | 52.6094 | 100 | 7.0686 | 9.4248 | 0.75 | 7.4427 | 0 | 0.4 | 0.34406 | 0.34406 | 37.8675
1320 | 36 | Pipe | 34 | 52.6094 | 100 | 7.0686 | 9.4248 | 0.75 | 7.4427 | 9.0583 |  | 0 | 9.0583 | 46.9259
| 36 | 45 Deg Bend | 34 | 52.6094 | 100 | 7.0686 | 9.4248 | 0.75 | 7.4427 | 0 | 0.4 | 0.34406 | 0.34406 | 47.2699
1320 | 36 | Pipe | 34 | 52.6094 | 100 | 7.0686 | 9.4248 | 0.75 | 7.4427 | 9.0583 |  | 0 | 9.0583 | 56.3282
| 36 | 90 Deg Bend | 34 | 52.6094 | 100 | 7.0686 | 9.4248 | 0.75 | 7.4427 | 0 | 0.2 | 0.17203 | 0.17203 | 56.5003
1320 | 36 | Pipe | 34 | 52.6094 | 100 | 7.0686 | 9.4248 | 0.75 | 7.4427 | 9.0583 |  | 0 | 9.0583 | 65.5586
| 36 | Exit to Headworks | 34 | 52.6094 | 100 | 7.0686 | 9.4248 | 0.75 | 7.4427 | 0 | 1 | 0.86015 | 0.86015 | 66.4187
[13 empty] | Total | 66.4187

## HL 35.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 35 | 54.1568 | 140 | 7.0686 | 9.4248 | 0.75 | 7.6616 | 0 | 0.25 | 0.22787 | 0.22787 | 0.22787
| 36 | 30" X 36" Increaser | 35 | 54.1568 | 140 | 7.0686 | 9.4248 | 0.75 | 7.6616 | 0 | 0.25 | 0.22787 | 0.22787 | 0.45575
1320 | 36 | Pipe | 35 | 54.1568 | 140 | 7.0686 | 9.4248 | 0.75 | 7.6616 | 5.1286 |  | 0 | 5.1286 | 5.5844
| 36 | 90 Deg Bend | 35 | 54.1568 | 140 | 7.0686 | 9.4248 | 0.75 | 7.6616 | 0 | 0.2 | 0.1823 | 0.1823 | 5.7667
1320 | 36 | Pipe | 35 | 54.1568 | 140 | 7.0686 | 9.4248 | 0.75 | 7.6616 | 5.1286 |  | 0 | 5.1286 | 10.8953
| 36 | 45 Deg Bend | 35 | 54.1568 | 140 | 7.0686 | 9.4248 | 0.75 | 7.6616 | 0 | 0.4 | 0.3646 | 0.3646 | 11.2599
1320 | 36 | Pipe | 35 | 54.1568 | 140 | 7.0686 | 9.4248 | 0.75 | 7.6616 | 5.1286 |  | 0 | 5.1286 | 16.3885
| 36 | 45 Deg Bend | 35 | 54.1568 | 140 | 7.0686 | 9.4248 | 0.75 | 7.6616 | 0 | 0.4 | 0.3646 | 0.3646 | 16.7531
1320 | 36 | Pipe | 35 | 54.1568 | 140 | 7.0686 | 9.4248 | 0.75 | 7.6616 | 5.1286 |  | 0 | 5.1286 | 21.8817
| 36 | 45 Deg Bend | 35 | 54.1568 | 140 | 7.0686 | 9.4248 | 0.75 | 7.6616 | 0 | 0.4 | 0.3646 | 0.3646 | 22.2463
1320 | 36 | Pipe | 35 | 54.1568 | 140 | 7.0686 | 9.4248 | 0.75 | 7.6616 | 5.1286 |  | 0 | 5.1286 | 27.3749
| 36 | 45 Deg Bend | 35 | 54.1568 | 140 | 7.0686 | 9.4248 | 0.75 | 7.6616 | 0 | 0.4 | 0.3646 | 0.3646 | 27.7395
1320 | 36 | Pipe | 35 | 54.1568 | 140 | 7.0686 | 9.4248 | 0.75 | 7.6616 | 5.1286 |  | 0 | 5.1286 | 32.8681
| 36 | 90 Deg Bend | 35 | 54.1568 | 140 | 7.0686 | 9.4248 | 0.75 | 7.6616 | 0 | 0.2 | 0.1823 | 0.1823 | 33.0504
1320 | 36 | Pipe | 35 | 54.1568 | 140 | 7.0686 | 9.4248 | 0.75 | 7.6616 | 5.1286 |  | 0 | 5.1286 | 38.1791
| 36 | Exit to Headworks | 35 | 54.1568 | 140 | 7.0686 | 9.4248 | 0.75 | 7.6616 | 0 | 1 | 0.91149 | 0.91149 | 39.0905
[13 empty] | Total | 39.0905
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 35 | 54.1568 | 100 | 7.0686 | 9.4248 | 0.75 | 7.6616 | 0 | 0.25 | 0.22787 | 0.22787 | 0.22787
| 36 | 30" X 36" Increaser | 35 | 54.1568 | 100 | 7.0686 | 9.4248 | 0.75 | 7.6616 | 0 | 0.25 | 0.22787 | 0.22787 | 0.45575
1320 | 36 | Pipe | 35 | 54.1568 | 100 | 7.0686 | 9.4248 | 0.75 | 7.6616 | 9.5573 |  | 0 | 9.5573 | 10.0131
| 36 | 90 Deg Bend | 35 | 54.1568 | 100 | 7.0686 | 9.4248 | 0.75 | 7.6616 | 0 | 0.2 | 0.1823 | 0.1823 | 10.1954
1320 | 36 | Pipe | 35 | 54.1568 | 100 | 7.0686 | 9.4248 | 0.75 | 7.6616 | 9.5573 |  | 0 | 9.5573 | 19.7527
| 36 | 45 Deg Bend | 35 | 54.1568 | 100 | 7.0686 | 9.4248 | 0.75 | 7.6616 | 0 | 0.4 | 0.3646 | 0.3646 | 20.1173
1320 | 36 | Pipe | 35 | 54.1568 | 100 | 7.0686 | 9.4248 | 0.75 | 7.6616 | 9.5573 |  | 0 | 9.5573 | 29.6747
| 36 | 45 Deg Bend | 35 | 54.1568 | 100 | 7.0686 | 9.4248 | 0.75 | 7.6616 | 0 | 0.4 | 0.3646 | 0.3646 | 30.0393
1320 | 36 | Pipe | 35 | 54.1568 | 100 | 7.0686 | 9.4248 | 0.75 | 7.6616 | 9.5573 |  | 0 | 9.5573 | 39.5966
| 36 | 45 Deg Bend | 35 | 54.1568 | 100 | 7.0686 | 9.4248 | 0.75 | 7.6616 | 0 | 0.4 | 0.3646 | 0.3646 | 39.9612
1320 | 36 | Pipe | 35 | 54.1568 | 100 | 7.0686 | 9.4248 | 0.75 | 7.6616 | 9.5573 |  | 0 | 9.5573 | 49.5186
| 36 | 45 Deg Bend | 35 | 54.1568 | 100 | 7.0686 | 9.4248 | 0.75 | 7.6616 | 0 | 0.4 | 0.3646 | 0.3646 | 49.8832
1320 | 36 | Pipe | 35 | 54.1568 | 100 | 7.0686 | 9.4248 | 0.75 | 7.6616 | 9.5573 |  | 0 | 9.5573 | 59.4405
| 36 | 90 Deg Bend | 35 | 54.1568 | 100 | 7.0686 | 9.4248 | 0.75 | 7.6616 | 0 | 0.2 | 0.1823 | 0.1823 | 59.6228
1320 | 36 | Pipe | 35 | 54.1568 | 100 | 7.0686 | 9.4248 | 0.75 | 7.6616 | 9.5573 |  | 0 | 9.5573 | 69.1801
| 36 | Exit to Headworks | 35 | 54.1568 | 100 | 7.0686 | 9.4248 | 0.75 | 7.6616 | 0 | 1 | 0.91149 | 0.91149 | 70.0916
[13 empty] | Total | 70.0916

## HL 36.0
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 36 | 55.7041 | 140 | 7.0686 | 9.4248 | 0.75 | 7.8805 | 0 | 0.25 | 0.24108 | 0.24108 | 0.24108
| 36 | 30" X 36" Increaser | 36 | 55.7041 | 140 | 7.0686 | 9.4248 | 0.75 | 7.8805 | 0 | 0.25 | 0.24108 | 0.24108 | 0.48216
1320 | 36 | Pipe | 36 | 55.7041 | 140 | 7.0686 | 9.4248 | 0.75 | 7.8805 | 5.403 |  | 0 | 5.403 | 5.8851
| 36 | 90 Deg Bend | 36 | 55.7041 | 140 | 7.0686 | 9.4248 | 0.75 | 7.8805 | 0 | 0.2 | 0.19286 | 0.19286 | 6.078
1320 | 36 | Pipe | 36 | 55.7041 | 140 | 7.0686 | 9.4248 | 0.75 | 7.8805 | 5.403 |  | 0 | 5.403 | 11.481
| 36 | 45 Deg Bend | 36 | 55.7041 | 140 | 7.0686 | 9.4248 | 0.75 | 7.8805 | 0 | 0.4 | 0.38573 | 0.38573 | 11.8667
1320 | 36 | Pipe | 36 | 55.7041 | 140 | 7.0686 | 9.4248 | 0.75 | 7.8805 | 5.403 |  | 0 | 5.403 | 17.2697
| 36 | 45 Deg Bend | 36 | 55.7041 | 140 | 7.0686 | 9.4248 | 0.75 | 7.8805 | 0 | 0.4 | 0.38573 | 0.38573 | 17.6554
1320 | 36 | Pipe | 36 | 55.7041 | 140 | 7.0686 | 9.4248 | 0.75 | 7.8805 | 5.403 |  | 0 | 5.403 | 23.0584
| 36 | 45 Deg Bend | 36 | 55.7041 | 140 | 7.0686 | 9.4248 | 0.75 | 7.8805 | 0 | 0.4 | 0.38573 | 0.38573 | 23.4442
1320 | 36 | Pipe | 36 | 55.7041 | 140 | 7.0686 | 9.4248 | 0.75 | 7.8805 | 5.403 |  | 0 | 5.403 | 28.8472
| 36 | 45 Deg Bend | 36 | 55.7041 | 140 | 7.0686 | 9.4248 | 0.75 | 7.8805 | 0 | 0.4 | 0.38573 | 0.38573 | 29.2329
1320 | 36 | Pipe | 36 | 55.7041 | 140 | 7.0686 | 9.4248 | 0.75 | 7.8805 | 5.403 |  | 0 | 5.403 | 34.6359
| 36 | 90 Deg Bend | 36 | 55.7041 | 140 | 7.0686 | 9.4248 | 0.75 | 7.8805 | 0 | 0.2 | 0.19286 | 0.19286 | 34.8287
1320 | 36 | Pipe | 36 | 55.7041 | 140 | 7.0686 | 9.4248 | 0.75 | 7.8805 | 5.403 |  | 0 | 5.403 | 40.2317
| 36 | Exit to Headworks | 36 | 55.7041 | 140 | 7.0686 | 9.4248 | 0.75 | 7.8805 | 0 | 1 | 0.96432 | 0.96432 | 41.196
[13 empty] | Total | 41.196
Length of Pipe | Diameter (in) | Item | Flow (MGD) | Flow (cfs) | C (Headloss Coefficient) | Pipe Cross sectional Area (ft2) | Pipe Perimeter (ft) | Hydraulic Radius (ft) | Velocity (ft/s) | Head Loss (ft) | Minor Loss K Coefficient | Minor Loss | Total Head Loss | Cumm. Head Loss (ft)
| 36 | 36" X 20" Reducer | 36 | 55.7041 | 100 | 7.0686 | 9.4248 | 0.75 | 7.8805 | 0 | 0.25 | 0.24108 | 0.24108 | 0.24108
| 36 | 30" X 36" Increaser | 36 | 55.7041 | 100 | 7.0686 | 9.4248 | 0.75 | 7.8805 | 0 | 0.25 | 0.24108 | 0.24108 | 0.48216
1320 | 36 | Pipe | 36 | 55.7041 | 100 | 7.0686 | 9.4248 | 0.75 | 7.8805 | 10.0686 |  | 0 | 10.0686 | 10.5508
| 36 | 90 Deg Bend | 36 | 55.7041 | 100 | 7.0686 | 9.4248 | 0.75 | 7.8805 | 0 | 0.2 | 0.19286 | 0.19286 | 10.7437
1320 | 36 | Pipe | 36 | 55.7041 | 100 | 7.0686 | 9.4248 | 0.75 | 7.8805 | 10.0686 |  | 0 | 10.0686 | 20.8123
| 36 | 45 Deg Bend | 36 | 55.7041 | 100 | 7.0686 | 9.4248 | 0.75 | 7.8805 | 0 | 0.4 | 0.38573 | 0.38573 | 21.198
1320 | 36 | Pipe | 36 | 55.7041 | 100 | 7.0686 | 9.4248 | 0.75 | 7.8805 | 10.0686 |  | 0 | 10.0686 | 31.2667
| 36 | 45 Deg Bend | 36 | 55.7041 | 100 | 7.0686 | 9.4248 | 0.75 | 7.8805 | 0 | 0.4 | 0.38573 | 0.38573 | 31.6524
1320 | 36 | Pipe | 36 | 55.7041 | 100 | 7.0686 | 9.4248 | 0.75 | 7.8805 | 10.0686 |  | 0 | 10.0686 | 41.7211
| 36 | 45 Deg Bend | 36 | 55.7041 | 100 | 7.0686 | 9.4248 | 0.75 | 7.8805 | 0 | 0.4 | 0.38573 | 0.38573 | 42.1068
1320 | 36 | Pipe | 36 | 55.7041 | 100 | 7.0686 | 9.4248 | 0.75 | 7.8805 | 10.0686 |  | 0 | 10.0686 | 52.1754
| 36 | 45 Deg Bend | 36 | 55.7041 | 100 | 7.0686 | 9.4248 | 0.75 | 7.8805 | 0 | 0.4 | 0.38573 | 0.38573 | 52.5612
1320 | 36 | Pipe | 36 | 55.7041 | 100 | 7.0686 | 9.4248 | 0.75 | 7.8805 | 10.0686 |  | 0 | 10.0686 | 62.6298
| 36 | 90 Deg Bend | 36 | 55.7041 | 100 | 7.0686 | 9.4248 | 0.75 | 7.8805 | 0 | 0.2 | 0.19286 | 0.19286 | 62.8227
1320 | 36 | Pipe | 36 | 55.7041 | 100 | 7.0686 | 9.4248 | 0.75 | 7.8805 | 10.0686 |  | 0 | 10.0686 | 72.8913
| 36 | Exit to Headworks | 36 | 55.7041 | 100 | 7.0686 | 9.4248 | 0.75 | 7.8805 | 0 | 1 | 0.96432 | 0.96432 | 73.8556
[13 empty] | Total | 73.8556