## CDM Template
INSERT SPU LOGO HERE | [10 empty] | EQUIPMENT DATA SHEET | [11 empty] | DATA SHEET NO. | [5 empty] | REV.
001
[23 empty] | SHEET |  | OF |  | DATE
[11 empty] | NO. |  | BY |  | DATE |  | REVISION | [5 empty] | 1 |  | 1 |  | 1/1/07
[11 empty] | 1 |  | MC |  | 1/1/07 | [7 empty] | BY |  | CHK'D |  | PROC. |  | APPR.
Project: |  | Example Pump Selection | [20 empty] | P.O.
REQ.
TAG/EQUIP NO: |  |  | PS-WPS -001 |  |  |  | Spec Section:: |  |  |  |  | 11306 |  |  |  | Location/Building: |  |  |  |  | Influent Pump Station
[7 empty] | Loop Wiring Diagram: | [8 empty] | Manufacturer: |  |  | Fairbanks Morse | [10 empty] | TRANSMITTER:
Asset No: |  | - |  |  |  |  | P&ID Sheet: |  |  |  |  | P-2 |  |  |  | Rep/Phone: |  |  | -
Name/Type: |  | wet pit submersible pump | [13 empty] | Model: |  |  | D5731 | [10 empty] | POWER: |  |  | POWER: |  |  |  |  | ELECTRICAL PROTECTION: |  |  |  | GAS GROUP: |  |  | TEMPERATURE CATEGORY: |  |  |  | ENCLOSURE PROTECTION: |  |  |  | LOCATION: | RELAY Type:
Service: |  | Wastewater | [13 empty] | Manufacturer: |  |  | - | [10 empty] | 24V DC |  |  | LOOP | 4 - 20 mA |  | ISOLATED |  | EX o |  |  |  | IIC |  |  | T1 |  |  |  | 0 |  |  | 0 | REMOTE | NONE
Spec Sht 1: | [6 empty] | Spec Sht 3: | [8 empty] | Rep/Phone: |  |  | - | [10 empty] | ~110 V AC 50/60 Hz |  |  | EXTERNAL | 0 - 5 V DC |  | SMART |  | EX p |  |  |  | IIC |  |  | T2 |  |  |  | 1 |  |  | 1 | INTEGRAL | N/C
Spec Sht 2: | [6 empty] | Spec Sht 4: | [8 empty] | Model: |  |  | - | [10 empty] | ~220 V AC 50/60 Hz |  |  | NA | PULSE |  | HART |  | EX q |  |  |  | IIB |  |  | T2A |  |  |  | 2 |  |  | 2 | NA | N/O
MECHANICAL | [13 empty] | ENVIRONMENTAL | [15 empty] | NA |  |  | SEE NOTES | 3 - 15 PSIG |  | SERIAL |  | EX d |  |  |  | IIA |  |  | T2B |  |  |  | 3 |  |  | 3 | SEE NOTES | NA
| Capacity: |  |  | 8,000 | [5 empty] | Units: |  | GPM |  |  | Pressure: | [5 empty] | Max |  |  |  | Min | Units: |  | PSI |  | SEE NOTES |  |  |  | NA |  | INDICATE |  | EX e |  |  |  | I |  |  | T2C |  |  |  | 4 |  |  | 4 |  | SEE NOTES
| Connection Size: |  |  | 14 | [5 empty] | Units: |  | Inches |  |  | Amb Temperature: |  |  | 95 |  |  | Max | 32 |  |  | Min | Units: |  | Deg F | [5 empty] | SEE NOTES |  | NA |  | EX ia |  |  |  | NA |  |  | T2D |  |  |  | 5 |  |  | 5
| Connection Type: |  |  | Flanged | [10 empty] | Location Occupancy Code: | [7 empty] | Site Specific Accel: | [12 empty] | SEE NOTES |  | EX ib |  |  |  | SEE NOTES |  |  | T3 |  |  |  | 6 |  |  | 6
| Size (LxWxH): |  |  | 72" X 39" X 116.5" | [5 empty] | Units: |  | Inches |  |  | Elevation: |  | 224 |  | Units: |  | ft |  | Seismic Zone: |  |  |  |  | 3 | [9 empty] | EX n | [6 empty] | T3A |  |  |  | NA |  |  | 7
| Operating Weight: |  |  | 5750 | [5 empty] | Units: |  | LB |  |  | Inside Building: |  |  |  |  | Confined Space | [5 empty] | Humidity: |  | >80% | [9 empty] | EX m | [6 empty] | T3B |  |  |  | SEE NOTES |  |  | 8
| Speed (Min/Max RPM): |  |  | 440/1200 | [10 empty] | Subject to Flooding: |  |  |  |  | Direct Sunlight: | [17 empty] | EX s | [6 empty] | T3C | [6 empty] | NA
| Mat'ls of Construction: |  |  | Cast Iron and Stainless Steel | [10 empty] | Dusty Area: |  |  |  |  | Corrosive Area: | [17 empty] | NA | [6 empty] | T4 | [6 empty] | SEE NOTES
| Accessories and Spare Parts: | [13 empty] | Damp W/D Area: |  |  |  |  | Freezing: | [17 empty] | SEE NOTES | [6 empty] | T4A
[15 empty] | Classified Area: |  |  |  |  | Class: |  | I | Div: |  | 2 | Group: |  | IIC | [16 empty] | T5
T6
ELECTRICAL | [13 empty] | MOTOR | [26 empty] | See Notes |  |  |  |  | NA
| Electrical Pwr: |  |  |  | Standby Pwr: |  |  |  |  | UPS: |  |  |  |  | Type: |  | Induction - Standard | [28 empty] | See Notes
| Voltage: |  |  |  | 480 VAC |  | Phase: |  | 3 |  | Wire: |  | 3 |  | Speed(s) (RPM): |  |  | 440 to 1200 |  |  |  |  | HP: |  |  | 250
| NEMA Enclosure Type: |  |  |  | 4X |  | IP Enclosure Type: |  |  |  | 54 |  |  |  | Enclosure: |  |  | SUBMERSIBLE |  |  |  |  | kW: |  |  | 187
| Continuous Amps: | [5 empty] | AIC (kAmps): | [7 empty] | NEMA Torque Design Code: | [7 empty] | Hertz: |  |  | 60
| UL Service Entrance: |  |  |  |  | Main Breaker (AT/AF): | [8 empty] | Estimated Starts/Hour: |  |  |  | 6 |  | Efficiency: |  |  | 80 |  | Pwr. Fct. |  | 1.15
| Rear Access Required: |  |  |  |  | Powered From: |  |  | EP and genrator | [5 empty] | Svc Fctr (Full Speed): | [6 empty] | Svc Fctr (VFD): | [8 empty] | ELECTRICAL:
| Two Exits Required: |  |  |  |  | Est. Heat Release (kW): | [8 empty] | ACCESSORIES AND FEATURES
| Design Operating Temp: |  |  |  |  | Units: | Deg F |  | HVAC Req'd | [5 empty] | Space Heater: |  |  |  | Chem Duty: | [5 empty] | Cntrl T Box: | [5 empty] | Voltage |  | NEMA ENCLOSURE TYPE |  |  | IP ENCLOSURE TYPE |  |  |  | Phase |  |  |  | Wire |  | Temp Units |  | VFD Pulses |  |  | Mounting |  | Elevation Unit |  |  | Motor LR Code | Motor Enclosure
| Variable Speed Drive: |  |  |  |  | Pulses: |  |  |  | AFE: |  |  |  |  | T'Stat: |  |  |  | Severe Duty: | [5 empty] | LR Code: | [5 empty] | 12 VDC |  | 1 |  |  | 10 |  |  |  | 1 |  |  |  | 2 |  | Deg C |  | 6 |  |  | Horizontal |  | cm |  |  | A | TEFC
| Harmonic Mitigation: | [13 empty] | RTD: |  |  |  | Inverter Duty: | [5 empty] | Insl Code: | [5 empty] | 24 VDC |  | 2 |  |  | 11 |  |  |  | 2 |  |  |  | 3 |  | Deg F |  | 12 |  |  | Vertical |  | ft |  |  | B | TENV
| Special Controls/Relays: | [13 empty] | Thermistors: |  |  |  | Tropical Duty: | [5 empty] | Mounting: |  | Vertical |  |  |  | 48 VDC |  | 3 |  |  | 14 |  |  |  | 3 |  |  |  | 4 |  | NA |  | 18 |  |  | NA |  | Inches |  |  | C | OPEN DRIP PROOF
| Accessories and Spare Parts: | [13 empty] | Mtr Vib Sw: |  |  |  | Bearing Vib Sw: | [11 empty] | 250VDC |  | 3R |  |  | 52 |  |  |  | NA |  |  |  | NA |  | SEE NOTES |  | 24 |  |  | SEE NOTES |  | NA |  |  | D | SUBMERSIBLE
[15 empty] | Mtr Vib Xmtr: |  |  |  | Bearing Vib Xmtr: | [11 empty] | 120 VAC |  | 4 |  |  | 54 | [7 empty] | SEE NOTES |  |  |  | NA |  |  |  |  | SEE NOTES |  |  | E | EXPLOSION PROOF
[31 empty] | 208 VAC |  | 4X |  |  | 65 | [11 empty] | SEE NOTES | [7 empty] | F | WPI
SPECIAL REQUIREMENTS | [13 empty] | INSTRUMENTATION | [16 empty] | 240 VAC |  | 6 |  |  | 56 | [19 empty] | G | NA
| Seal Water: |  |  |  | Air Supply: |  |  |  | Drain: | [5 empty] | Process Var: | [6 empty] | Sensor Type: | [8 empty] | 277 VAC |  | 7 |  |  | 67 | [19 empty] | H | SEE NOTES
| Painting/Coating: |  | Coating suitable for wastewater service (epoxy) | [11 empty] | Accuracy: |  |  |  | Ops Range: | [5 empty] | Units: |  | PERCENT |  |  |  | 120/208 VAC |  | 8 |  |  | 68 | [19 empty] | J
| Special O&M, Environmental, or Equipment Specific Information, etc. | [13 empty] | Repeatability: |  |  |  | Calib Range: | [5 empty] | Units: |  | PERCENT |  |  |  | 120/240 VAC |  | 9 |  |  | NA | [19 empty] | K
| Owner Furnished: |  |  |  | GC Furnished: | [9 empty] | Setting: | [9 empty] | Units: |  | PSI |  |  |  | 277/480 VAC |  | 10 |  |  | SEE NOTES | [19 empty] | L
[15 empty] | Output (mA): |  | 4 to 20 mA |  |  |  |  | Voltage: |  |  | 480 VAC | [5 empty] | 240/480 VAC |  | 11 | [22 empty] | M
[15 empty] | Pneumatic |  |  |  | Hydraulic: |  |  |  |  | Input to DCS: | [6 empty] | 480 VAC |  | 12 | [22 empty] | N
[15 empty] | Fieldbus Type: | [6 empty] | Monitored From: | [8 empty] | 4160 VAC |  | 13 | [22 empty] | P
[15 empty] | Wetted Parts Materials: | [15 empty] | NA |  | NA | [22 empty] | R
[15 empty] | Int Safe: |  |  |  | Packgd by Mfgr: | [5 empty] | Dia. Seal: | [5 empty] | SEE NOTES |  | SEE NOTES | [22 empty] | S
[15 empty] | NEMA Enclosure Type: |  |  |  |  | 4X |  |  | IP Enclosure Type: |  |  |  | 54 | [28 empty] | T
[15 empty] | ALARMS SETPOINTS | [40 empty] | U
[15 empty] | Hi-Hi: | 244 |  | Hi: |  | 240 |  | Lo: |  | 232 |  | Lo-Lo: |  | 228 | [27 empty] | V
NA
NOTES | Also need to monitor motor and pump run time, speed, and temperature and vibration. | [54 empty] | SEE NOTES
[31 empty] | Pressure | NEMA Torque Design Code |  |  | Class |  | Division |  | Hertz |  |  |  | Motor Insulation Code |  |  |  | Accuracy |  |  | Instru. Output (mA) |  |  | Weight |  | Capacity Unit |  | Motor types
[31 empty] | PSI | A |  |  | I |  | 1 |  | 50 |  |  |  | A |  |  |  | F |  |  | 4 to 20 mA |  |  | LB |  | GPM |  | Induction - Standard
[31 empty] | PSIA | B |  |  | II |  | 2 |  | 60 |  |  |  | B |  |  |  | FT |  |  | NA |  |  | Kg |  | Gallons |  | Induction - Premium Efficiency
[31 empty] | BAR | C |  |  | III |  | NA |  | NA |  |  |  | F |  |  |  | FT ABF |  |  | SEE NOTES |  |  | g |  | CFM |  | Synchronous
DIST | (ATTACH CATALOG CUTS AS NECESSARY) | [29 empty] | NA | D |  |  | NA |  | SEE NOTES |  | SEE NOTES |  |  |  | H |  |  |  | FT AFF | [5 empty] | NA |  | CSF |  | DC Drive
| PM |  |  | DNDF |  |  |  | I&C |  |  |  |  | SPEC | [17 empty] | SEE NOTES |  |  |  | SEE NOTES | [7 empty] | NA |  |  |  | GPM | [5 empty] | SEE NOTES |  | Liter/Day |  | NA
| PE |  |  | ELECTRICAL |  |  |  | MECHANICAL |  |  |  |  | STRUCT | [18 empty] | NA | [10 empty] | SEE NOTES |  |  |  | IN ASF | [7 empty] | NA |  | SEE NOTES
| ARCH |  |  | ESTIMATOR |  |  |  | PLUMBING |  |  |  |  | CLIENT 1 | [18 empty] | SEE NOTES | [14 empty] | IN HG VAC | [7 empty] | SEE NOTE
| CIVIL |  |  | HVAC |  |  |  | PROCESS |  |  |  |  | CLIENT 2 | [33 empty] | MGD
E:\Ch11_v.2_FinaltoSPU\AppxD_EquipData\[AppDequipmentdatasheettemplate.xls]CDM Template | [23 empty] | 2010-08-16 08:08 | [22 empty] | MICRONS
MICRONSIEMENS/CM
This example template has not been reviewed or approved for wide-use, and is provided as informational only for now. The engineer may use this, but it should be thoroughly checked. | [46 empty] | NTU
PERCENT
pH
PPM
PSI
PSIG
NA
SEE NOTES
Solenoid & Switches
Electric Valve Actuator
Notes
Solenoid
Electric Valve Actuator
Switches
Note on AG26: Gas / Dust Groups IIC - Acetylene IIC - Hydrogen IIB - Ethylene IIA - Propane I - Methane