## EV Assessment
City of Seattle
Department of Planning and Development
700 5th Ave, Suite 2000, PO Box 34019, Seattle, WA 98124-4019
Directions: Select each box for a drop down list and select your specific information.
Preliminary Assessment of Single-Family Home EV Capacity
(Approximate time for assessment: 5 min)
1) Does the panel board have screw-in fuses? | [5 empty] | N o
a. Yes (end assessment here)*
b. No
2) What is the electrical capacity of the panel board? | [5 empty] | 125 Amp
a. 100 Amp (end assesment here)*
b. 125 Amp
c. 200 Amp
d. Above 200 Amp
3) Does the panel board have two empty circuits available? This can be determined by pre-pressed slots in the panel cover that touch vertically not horizontally.
a. Yes | [5 empty] | Yes
b. No (end assessment here)*
* In some instances the pre-pressed slots can be misleading and actually not have the available bussing required for the new breaker to attach to.
4) What is the approximate square footage of the home?
Square Feet (Pick the closest) | [5 empty] | 3500
Assumed Wattage
5) If the home has natural gas service service, please check which appliances are served by natural gas.
a. Furnace Breaker: | [5 empty] | 2-pole 60A |  |  | 11520
b. Water Heater (HWT) | [5 empty] | Electric |  |  | 4500
c. Dryer | [5 empty] | Electric |  |  | 5000
d. Stove |  |  | Range/Oven |  |  | Electric |  |  | 10500
e. Hot Tub/Jacuzzi | [5 empty] | Electric |  |  | 10000
6) Does the home have any of the following:
a. Electric Zone Heat (individual heaters) | [6 empty] | Yes |  | 17500
b. Heat Pump: | [6 empty] | 2 Ton |  | 7000
c. Air Conditioner | [6 empty] | 2 Ton |  | 7000
d. Other significant electric equipment beyond the standard appliances: A second stove, water heater, washer, or dryer. Other equipment could include a kiln, welder or compressor.
|  |  | Appliance 1 |  |  |  | Second Range |  | 10500
|  |  | Appliance 2 |  |  |  | Second Washer |  | 1500
|  |  | Appliance 3 |  |  |  | Detached Building |  | 9600
|  |  | Car Charger |  |  |  | 40 Amp 240V |  | 9600
7) Where is the the electrical panel board located in the home?
Garage
| 8) | Load Calculation |  | 253.9292 | Amps
* If you have not ended this assessment per items 1, 2 or 3 above and have been able to calculate all the electric loads and the total load calculation on line 8 is less than 125 amps, a 125 amp service should be sufficient. If you are not able to calculate all appliance and heat loads, a more thorough assessment is needed. The same principle applies to a 200 amp service.
This is an approximate calculation further additional information may be required.

## Calculation (hidden)
UNIT: | Quantity | Load each | W | Feeder | W | Neutral | W
LIGHTING | 3500 | 3 | W | 10500 | W | 10500 | W
APPLIANCE | 2 | 1500 | W | 3000 | W | 3000 | W
2nd kitchen APPLIANCE | 2 | 1500 | W | 3000 | W | 3000 | W
WASHER | 1 | 1500 | W | 1500 | W | 1500 | W
2ND WASHER | 1 | 1500 | W | 1500 | W | 1500 | W
DRYER | 1 | 5000 | W | 5000 | W | 3500 | W
2ND DRYER | 0 | 5000 | W | 0 | W | 0 | W
DISHWASHER | 1 | 1500 | W | 1500 | W | 1500 | W
2ND DISHWASHER | 1 | 1500 | W | 1500 | W | 1500 | W
MICROWAVE | 1 | 1500 | W | 1500 | W | 1500 | W
2ND MICROWAVE | 1 | 1500 | W | 1500 | W | 1500 | W
DISPOSAL | 1 | 750 | W | 750 | W | 750 | W
DISPOSAL | 1 | 750 | W | 750 | W | 750 | W
WATER HEATER | 1 | 4500 | W | 4500 | W |  | W
2ND WATER HEATER | 0 | 4500 | W | 0 | W |  | W
RANGE | 1 | 10500 | W | 10500 | W | 7350 | W
2ND RANGE | 1 | 10500 | W | 10500 | W | 7350 | W
HOT TUB | 1 | 10000 | W | 10000 | W | 7000 | W
KILN | 0 | 9600 | W | 0 | W | 0 | W
COMPRESSOR | 0 | 7200 | W | 0 | W |  | W
DETACHED BUILDING | 1 | 9600 | W | 9600 | W | 9600 | W
WELDER | 0 | 10500 | W | 0 | W | 0 | W
Electric Vehicle Charger | 1 | 9600 | W | 9600 | W | 0 | W
Gas Furnace | 0 | 1200 | W | 0 | W | 0 | W
HEAT PUMP | 1 | 7000 | W | 7000 | W |  | W
AIR CONDITIONER | 1 | 7000 | W | 7000 | W |  | W
TOTAL |  |  |  | 90200 | W | 51300 | W
FIRST 10 KW AT 100% |  |  |  | 10000 | W | 10000 | W
REMAINING X 40% |  |  |  | 32080 | W | 16520 | W
HEAT (3 or 4 zones) | 1 | 11520 | W | 7488 | W
HEAT (3 or 4 zones) | 1 | 17500 | W | 11375 | W
TOTAL CONNECTED LOAD |  |  |  | 60943 | W | 26520 | W
DIVIDED BY VOLTAGE | 240 |  |  | 253.9292 | A | 110.5 | A

## constant (hidden)
Yes |  | amp |  | Square feet | Furnace |  | Location |  | hwt |  | dryer |  | Hottub
N o |  | 100 Amp |  | 1000 | 1pole 20A(Gas) | 1200 | Garage |  | Electric | 4500 | Electric | 5000 | Electric | 10000
|  | 125 Amp |  | 1250 | 2-pole 60A | 11520 | Unfinished Basement |  | Gas | 0 | Gas | 1200 | Gas | 1500
|  | 200 Amp |  | 1500 | 2-pole 30A &2-pole 60A | 17280 | Finished Basement | [5 empty] | N/A | 0
|  | Above 200 Amp |  | 2000 |  |  | Other Location
|  |  |  | 2500 | 2-pole 60A &2-pole 60A | 23040
3000
|  |  |  | 3500 | N/A | 0
range |  |  | Electricheat |  | MiscApp |  | misc | HeatPump |  | AC |  |  | Cars
Electric | 10500 |  | Yes |  | N/A |  |  | 2 Ton | 7000 | 2 Ton | 7000 |  | 20 Amp 120V |  | 2400
Gas | 1200 |  | No |  | Second Range |  | 10500 | 3 Ton | 10500 | 3 Ton | 10500 |  | '15 Amp 240V |  | 3600
[5 empty] | Second Dryer |  | 5000 | 4 Ton | 14000 | 4 Ton | 14000 |  | 20 Amp 240V |  | 4800
[5 empty] | Second Washer |  | 1500 | N/A |  | N/A |  |  | 30 Amp 240V |  | 7200
[5 empty] | Second HWT |  | 4500 | [5 empty] | 40 Amp 240V |  | 9600
[5 empty] | Welder |  | 10500 | [5 empty] | 50 Amp 240V |  | 12000
[5 empty] | Compressor |  | 7200
[5 empty] | Kiln |  | 9600
[5 empty] | Detached Building |  | 9600
Cars
[13 empty] | 20 Amp 120V |  | 2400
[13 empty] | 15 Amp 240V |  | 3600
[13 empty] | 20 Amp 240V |  | 4800
[13 empty] | 30 Amp 240V |  | 7200
[13 empty] | 40 Amp 240V |  | 9600
[13 empty] | 50 Amp 240V |  | 12000