## Slide 1: Eastside Reservoir Site Drainage and Leakage Issues

## Slide 2: Background – Eastside Reservoir
Transmission/regional asset – in Bellevue
Buried concrete reservoir
  32 million gallons
  Constructed late 1980’s
  2-ft soil cover, no public access

## Slide 3: Issues
Groundwater leaking into reservoir (today’s topic)
  Via roof-to-wall joint (direct access)
  Via standing water on the soil cover (slow permeation through concrete roof)
Treated water has almost always leaked out more than AWWA standards (being addressed separately by SPU crews)

## Slide 4: Roof-to-Wall Joint
A movable joint between roof and wall allows for roof to expand and contract separately from the wall
  Different design than newer buried reservoirs
Joint is “stepped,” meant for seismic (lateral force) resistance
  Seismic calcs appear to be adequate

## Slide 5: Roof-to-Wall Joint
Stepped joint has filler in vertical sections

## Slide 6: Roof-to-Wall Joint
An exterior cover over the joint is designed to prevent groundwater from entering through any gaps in the joint

## Slide 7: Roof-to-Wall Joint
Joint has moved laterally, resulting in gaps between vertical faces
Exterior joint cover has failed
Groundwater flowing through gaps

## Slide 8: Groundwater Leaks Through Roof
Standing water after rains
No waterproofing layer over reservoir roof
No roof drain piping around perimeter
Standing water permeates slowly through roof concrete

## Slide 9: Discussion
No regulatory issues with design back in 1980’s
DOH recent sanitary survey:
  Roof-to-wall joint leaks are a “significant deficiency”
  Roof permeation should be addressed (but not uncommon)
SPU agreed to address both issues
  Can still operate reservoir while developing path forward

## Slide 10: Recommendations
Roof-to-wall joint leaks
  Dig up exterior joint cover and replace
  Improve site drainage by adding roof drain piping in a drain trench around the perimeter
Roof permeation
  Add drains on roof

## Slide 11: Design – Roof Drains

## Slide 12: Design – Roof Drain Ring

## Slide 13: Design – Waterproofing

## Slide 14: Next Steps
Work being bid now
Construction over summer 2015